Kire Popovski, Stojance Nusev, Igor Andreevski
Ring-type water supply networks

ring-type water SUPPLY networkS

Kire Popovski1, Stojance Nusev2, Igor Andreevski3
Summary: Standard calculation of water supply networks takes a lot of time and requires high accuracy while computer programmes for this purpose are very expensive. A computer program has been made to reduce the calculation time and to increase the accuracy of the calculation with no additional cost. The program is fully automatic and does not require previous experience and advanced computer knowledge to operate it. There are two types of water supply networks, branched and ring-type. Ring type consists of a series of closed loops (rings) surrounding the consumers and supply them with water through branches (sections). This type of water supply networks has an advantage over branched type because they do not require stopping of water in the entire network in a case of exclusion of certain parts of the network. When all input parameters are known, it is necessary to calculate the diameters of all sections and meet the required pressure drop in each of them.

Key words: ring water supply networks.
1. introduction

According to hydraulic connections, there are two types of water supply networks, branched and looped (ring-type). Looped water supply network, Fig. 1, consists of a number of closed loops (rings) surrounding the consumers while supplying them with water through sections. This king of network has advantage over branched type because there is no need to interrupt the supply to all network if and intervention is required only on one part of it. When calculation for looped type of water supply network is performed, two laws of hydraulics have to be satisfied:


- The sum of volume flows in every node must to be zero, that is the amount of water entering and leaving the node must be equal and


- At constant flow, the pressure difference between two cross-sections in the network is used to overcome the resistance and geodetic height between the cross-sections.


In order to explain the mathematical model, which used as a base for development of computer programme, an example shown in Figure 1 is used. Every branch is labeled with number and the corresponding volume flow (ex. 1-14 means branch 1, 14 l/s). Network is comprised of 4 loops also labeled with numbers in the middle. To run the computer programme properly, it has to be previously "filled" with input data (with known network data).

[image: image1.jpg]



Fig. 1. Ring - type water supply network


Volume flow (inlet and outlet) and length of section represent input data for every node.

Total allowed pressure drop in the system is p=5000 Pa, [1]. This value of pressure drop is enough to allow the complete calculation of the network to be with satisfying accuracy, but the computer programme itself allows the total pressure drop in some cases to reach values smaller than 100 Pa. 

Number of loops: j = 4

Number of sections: i = 12

Friction coefficient of the pipe: =0,018

Density of water: =1000 kg/m3
For calculation of the network parameters, relative direction of water movement in the loops have to be adopted. In this case, we adopt clockwise direction to be 'positive'.

With above shown input data it is neccessary to calculate cross-sections of all section and to match the allowed pressure drop in each of them.

The calculation goes under the following order:

Pipe diameter,
 
[image: image2.wmf](

)

48

,

0

025

,

0

i

i

q

D

×

×

=

r

 m.

Calculated diameter is standardized onto the first greater standard size.

Recommended values for velocity of water in pipes are, w=0,75 - 2 m/s.

Hydraulic resistances,

[image: image3.wmf]33

,

5

01454

,

0

-

×

×

×

=

i

i

i

D

L

S

r

 Pa∙s2/m6.

Energy losses due to friction (pressure drop),


[image: image4.wmf]2

i

i

i

q

S

p

×

=

D

 Pa.

Correction of the flow in the loop,


[image: image5.wmf]i

i

i

j

q

S

p

q

å

å

×

×

D

-

=

D

2

 m3/s.

2. NumeriCAL EXAMPLE


Calculation is performed through iterations while the number of iterations is determined by the value of pressure drop, i.e. number of iterations must be sufficient to result in pressure drop equal or smaller than recommended value.

Table 1. Review of calculate water flow in each iteration 

	Section
	l
m
	q

l/s
	q – 1

l/s
	q - 2

l/s
	q - 3

l/s
	d

mm
	p
Pa

	1
	880.000
	14.000
	9.410
	9.241
	9.233
	100.0
	234975

	2
	735.000
	30.000
	32.242
	32.362
	32.362
	151.0
	267734

	3
	880.000
	180.000
	185.000
	185.469
	185.445
	313.9
	212451

	4
	735.000
	45.300
	36.760
	36.593
	36.602
	160.3
	249003

	5
	880.000
	15.000
	14.280
	14.281
	14.241
	100.0
	559026

	6
	735.000
	15.000
	16.305
	16.304
	16.365
	100.0
	616599

	7
	880.000
	63.300
	64.744
	63.719
	63.708
	211.1
	208051

	8
	735.000
	15.000
	15.908
	16.739
	16.739
	100.0
	645149

	9
	880.000
	15.000
	14.485
	15.035
	15.035
	100.0
	623128

	10
	735.000
	30.100
	30.722
	29.906
	29.909
	151.0
	228694

	11
	880.000
	20.700
	18.623
	18.291
	18.275
	125.0
	280049

	12
	735.000
	65.100
	62.434
	62.163
	62.147
	211.1
	165357


Number of iteration depends on the accuracy determined in the computer programme. In this case, the accuracy is set to 0,11 l/s which means that the difference between calculated flow in the section from the previous iteration and currently calculated flow in the same section should not be greater than 0,1 l/s.

 Accuracy of mathematical model and computer programme is proved by comparing with the same network calculated according to [1]. Comparison is presented on Table 2.

Table 2. Comparison of results

	Section
	Starting flow

l/s
	Calculated

flow

l/s
	Calculated flow

l/s

according to [1]
	l

m
	d

mm
	d

mm

according to [1]

	1
	14.000
	9.233
	9.470
	880
	100.0
	150

	2
	30.000
	32.362
	32.500
	735
	151.0
	200

	3
	180.000
	185.445
	190.480
	880
	313.9
	400

	4
	45.300
	36.602
	40.770
	735
	160.3
	200

	5
	15.000
	14.241
	12.970
	880
	100.0
	150

	6
	15.000
	16.365
	17.030
	735
	100.0
	150

	7
	63.300
	63.708
	67.580
	880
	211.1
	300

	8
	15.000
	16.739
	17.250
	735
	100.0
	150

	9
	15.000
	15.035
	12.750
	880
	100.0
	150

	10
	30.100
	29.909
	33.800
	735
	151.0
	200

	11
	20.700
	18.275
	14.750
	880
	125.0
	150

	12
	65.100
	62.147
	59.150
	735
	211.1
	250


3. Nomenclature

d
diameter of the section,

H
geodetic height of node in the network,

l
length of section,

p
pressure in network,

q
volume flow of water in section,

w
velocity of water in section,

p 
energy loss due to friction.

4. references
[1] Šašić, M. (1982). Transport fluida u cevima, Mašinski fakultet, Beograd, Srbija.

[2] Stojanovski V., Popovski K. (2004). Transportni sistemi i transport vo cevki, Zbirka na rešeni i ispitni zadači, I del, Tehnički fakultet, Bitola, Makedonija.

[3] Dymond J.H., Nieto de Castro C.A. (1996). Transport properties of fluids: their correlation, prediction and estimation, Cambridge University Press, UK.

[4] Swamee P.K., Sharma K.A. (2008). Design of water supply pipe networks, Wiley-interscience.






_______________________________________________________________________________________

1 Vanr. prof. d-r. Kire Popovski, Bitola,Faculty of Technical Sciences, Macedonia,kire.popovski@uklo.edu.mk
2 Red. prof. d-r. Stojance Nusev, Bitola, Faculty of Technical Sciences, stojance.nusev@uklo.edu.mk
3 Doc. d-r. Igor Andreevski, Bitola, Faculty of Technical Sciences, igor.andreevski@uklo.edu.mk

_1069408162.unknown

_1069408205.unknown

_1069408228.unknown

_1069408071.unknown

