Dumonjić-Milovanović Svetlana, Petar Gvero
Optimization of hybrid system for electricity production based on wind and Sun energy conversion with analysis of its applicability on Banja Luka region

[image: image1.jpg]



OPTIMIZATION OF HYBRID SYSTEM FOR ELECTRICITY PRODUCTION BASED ON WIND AND SUN ENERGY CONVERSION WITH ANALYSIS OF ITS APPLICABILITY ON BANJALUKA REGION

Svetlana Dumonjic-Milovanović
, Petar Gvero

Summary: Globally increased energy requirements indicate the necessity for introduction of energy saving measures, necessity for applying energetic efficiency as well as more active usage of sustainable energy sources in production of the electricity. One of the possible ways to introduce sustainable energy sources certainly are systems for production of electricity which are based on energy of the Sun and on the wind energy. Because of intense stochasticism of the nature of primary energy sources, there certainly is present the need for their optimization. Thereat, the technical capacities are in dependence with available wind and Sun potential, so with the needs of observed consumer or with possibility to sell the energy inside the program of obligatory redemption. Inside this paper the analysis of optimal usage of the wind energy and the energy of Sun by virtue of hybrid systems in terms of supplying small consumers on Banjaluka region with the electricity  is given. The research was performed by methods for predictive analysis of primary energy sources and their combinations, and so by the algorithm for defining optimal ratio of certain forms of energy according to accepted technical and economic criteria (the lowest price of electricity produced by the hybrid system, availability of the energy, etc.) The resulting data is in compliance with Banjaluka region. The performed method for optimizing and economic-financial analysis has confirmed construction justifiability of systems based on wind and Sun energy. 

Key words: hybrid system, wind energy, Sun energy, optimization, electricity cost, Banja Luka region
1. INTRODUCTION 
The wind and radiation from the Sun both do have stochastic character. The stochasticity affects on a daily, monthly, seasonal and on the level of a year in a whole. If the weather conditions are convenient, the Sun energy is available only from sunrise till sundown, and it also depends on seasonal alternations of trajectory of the Earth while circling around the Sun. Presence of the wind is higher, but on the region of Banja Luka its intensity is rather low. Coupled usage of those two energy sources increases availability of the energy in total. This approach in some extent reduces limitations resulting from their insufficient individual availability. 
In distant locations, where electric grid is not available, the necessity for supplying with electricity through alternative sources is significant. As one of the solutions, regarding that issue is the possibility of appliance of autonomous hybrid systems based on exploitation of the Sun and wind energy.  The aim of the project was to define optimal configuration of the system represents the configuration which can achieve the lowest price of produced energy (the lowest energy equivalent), predicted to be used in rural off-grid areas 

2. INPUT DATA IN PROCESS OF OPTIMIZATION
Available data for the wind of Banja Luka region are presented as average values of the wind speed sorted by months and with associated rate of silence. Randomized model of the wind speed alteration on the level of one hour is acquired in compliance with Weibull distribution with tolerance of scale parameter of 0.2 and shape parameter of 0.1. Conducting the simulation a variety of possible scenarios were acquired according to which the time dependent distribution of the wind speed can be in progress during the year. One of those results is shown on Figure 1.
[image: image2.jpg]Wind speed, m/s

Stochastic model of wind speed alteration, mfs
Average wind speed according to model, m/s

LRSS

500 1000 1500 2000 2500

3000

300 DD 4500 BOO0  AOD
Time. h

6000

6500

7000 7500 8000 SO0





 Fig. 1   Randomized scenario of possible wind speed alteration during the year with monthly mean values of the wind speed, Banja Luka
On the basis of the wind speed model alteration on the level of the one hour the energy production forecast has been made for the wind turbine with cut-in speed of 2 m/s on a daily level.

The calculation of global radiation (based on the available data of measured global radiation on horizontal surface and other available meteorology data) was carried out on principal of altering of certain values of daily clearness index of the atmosphere. Through that method the randomized model of radiation for every angle of surface inclination has been created. On Figure 2 the review of randomized scenario of radiation for horizontal surface for the region of Banja Luka is given. 
This model has been used for forecasting average production of the energy on daily level on unit surface area of polycrystalline photovoltaic panel. 
[image: image3.jpg]Global radiation, W/m2

j L : i i
| i i \Q\ i

CHRMIRRIL Ty s T

S0 1000 1500 200 2600 00 00 AG0 450 5000 500
Time, h

Stochastic model o radiation, horizontal surface
Average value of radiation, Wiini2, day=24 hours

Il
il IJ I
[im

Hhi
] HHMIHHW TR e S
6000 6500 7000 7500 B000 8500





Fig. 2   Randomized scenario of possible radiation intensity alteration during the year with mean monthly values for region of Banja Luka, horizontal surface
For determining investment costs of hybrid system design, prices of certain components have been adopted and presented in units of nominal measure (Table 1). Costs of current maintenance of the system was adopted to be 2% from starting investment on annual level. Besides that, costs related to expenses of the unforeseen additional labor and equipment, consulting services, insurance, concession reimbursement, expenses of loan processing, interests, etc. were also adopted to be 10% from starting investment (1KM = 0.51129EUR).
Table 1  Prices of certain hybrid systems components presented in units of nominal measure 
	Item
	Value
	Unit
	Symbol

	HAWT
	3800.00
	KM/kWnom
	cWT

	Additional costs of wind turbine pole
	280.00
	KM/kWnom/m
	cTWT

	Polycrystalline photovoltaic panel
	3900.00
	KM/kWnom
	cPV

	PV panel support and fastening equipment
	480.00
	KM/m2
	cCPV

	Electric components - controller
	900.00
	KM/kWnom
	cEK

	Electric components - inverter
	500.00
	KM/kWnom
	cEI

	Electric components - electricity meter
	300.00
	KM/kWnom
	cEB

	Batteries
	400.00
	KM/kWnom
	cBAT

	Diesel electric power unit
	1400.00
	KM/kWnom
	cDA


3. CHOOSING OPTIMAL CONFIGURATION OF THE HYBRID SYSTEM
Calculating of excess or lack of the energy 
[image: image4.wmf](

)

load

kWh

kWh

e

,

D

 in relation to the energy produced on a daily level is done by usage of calculated values of produced energy (
[image: image5.wmf]hibW

e

 and 
[image: image6.wmf]2

/

,

m

kWh

e

hibS

) and relative surface areas of applied wind turbine and photovoltaic panel (
[image: image7.wmf]W

a

 and 
[image: image8.wmf]S

a

) expressed through the ratio of real active surface area and average daily consumption of the energy 
[image: image9.wmf](

)

load

kWh

m

/

2

, and is given by: 
                           
[image: image10.wmf]1

-

×

+

×

=

D

hibS

S

hibW

W

e

a

e

a

e

.                                       (1)
Program for optimizing of autonomous system encounters calculation of electricity production from diesel power unit during the year in terms of auxiliary power supply inside the system 
[image: image11.wmf](

)

load

DAy

kWh

kWh

e

,

. Inside the calculating the costs of diesel power unit drive, the price of diesel fuel 
[image: image12.wmf](

)

DF

c

 has been adopted to be 2.4 KM/l and diesel fuel consumption 
[image: image13.wmf](

)

DF

l

 to be 0.4 l/kWh. Also through the program for optimizing of the grid connected hybrid system the calculating of annual rate of each category of the energy, given or taken from the grid 
[image: image14.wmf](

)

GRIDy

y

GhibS

GhibWy

e

e

e

,

,

, presented by daily unit consumption of the energy 
[image: image15.wmf](

)

load

kWh

kWh

 has been foreseen.
Prices of the energy acquired from the system (equivalent energy, 
[image: image16.wmf]load

kWh

KM

) arises from the applied equations:


[image: image17.wmf](

)

(

)

(

)

(

)

(

)

(

)

(

)

,

365

365

25

.

1

2

.

1

01

.

0

1

.

1

2

365

02

.

0

1

.

1

DF

DF

DAy

y

EK

BAT

d

EI

DA

y

y

CPV

PV

r

S

TWT

WT

W

Wnom

W

y

E

l

c

e

no

c

c

no

c

c

peak

no

no

c

c

a

h

c

c

A

P

a

no

c

×

×

+

×

+

×

×

+

+

×

×

×

×

+

×

+

+

×

÷

÷

ø

ö

ç

ç

è

æ

+

×

×

+

×

+

×

×

×

×

+

=

h

 (2)
for autonomous systems and

[image: image18.wmf](

)

(

)

(

)

(

)

(

)

,

365

365

01

.

0

1

.

1

2

365

02

.

0

1

.

1

max

GhibS

GhibSy

GhibW

GhibWy

GRID

GRIDy

y

y

EB

EI

y

CPV

PV

PV

S

TWT

WT

W

Wnom

W

y

E

c

e

c

e

c

e

no

no

c

c

ex

no

c

c

a

h

c

c

A

P

a

no

c

×

-

×

-

×

+

×

×

+

×

+

×

×

+

+

×

÷

÷

ø

ö

ç

ç

è

æ

+

×

×

+

×

+

×

×

×

×

+

=

h

 (3)
for the grid connected system. In this case the amount of 
[image: image19.wmf]GRID

GhibS

GhibW

c

c

c

,

,

 depends on prices of the energy inside the program of obligatory buyout and the energy taken from the grid, 
[image: image20.wmf]max

ex

 is the maximal value of the relative energy flow, 
[image: image21.wmf]load

kWh

kWh

, and 
[image: image22.wmf]y

no

 is the lifetime.
The results of optimizing are given on Figures 3 to 5. On Figure 6 the result of optimizing for conditions with average wind speed of 5 m/s is given.

[image: image23.jpg]Banja Luka, WG 1000W/3.33m2, PVI38W2, autonomous system
actiimiation 3 days

i
i

=
===
RIS
———

Equivalent energy, KM/kWh

Relative surface area WG, aw 5
e 0s Relative sufface area PV, as

4.5

a4

.2

8

36

B4

52

b8

o5




Fig. 3   Result of optimizing for Banja Luka region, PV  poly 139W/m2, WG HAWT 1000W/3.33 m2, peak=0.7, accumulation 3 days
[image: image24.jpg]Banja Luka, WG 1000W/3:33112, PVI38W/m2, autonomous system
accumulation 1 day

Equivalent energy, KM/kWh

3

Relatissurdce/area o aw: Relative surface area PV, as

8

36

54

5.2

0.8

06

D4

D2

1.8




Fig. 4   Result of optimizing for Banja Luka region, PV  poly 139W/m2, WG HAWT 1000W/3.33 m2, peak=0.7, accumulation 1 day

[image: image25.jpg]Equivalent energy, KM/kWh

Relative surface area WG, aw

Banja Luka, WG 1000W/3.33m2, PV 139W/m2, grid connected system

Relative surface area PV, as

18

15

1.4

1.2

ns

i

0.4




Fig. 5   Result of optimizing for Banja Luka region, PV  poly 139 W/m2, WG HAWT 1000W/3.33m2, grid connceted system
[image: image26.jpg]Equivalent energy, KM/kWh

Relative surface area WG, aw

Average wind speed 5 mfs, WG AD0DW/14.41m2, PVI39Wim2, autonomous systern
dEcumulation 1 day

Relative surface area PV, as

ok

X

.4

P2

18

15

1.4




Fig. 6   Result of optimizing for average wind speed of  5 m/s, PV  poly 139 W/m2, WG VAWT 4000W/14.41m2, peak=0.2,  accumulation 1 day
4. CONCLUSION
Results of optimizing have approved annotation related on very weak potential of the wind on the region of Banja Luka. The most convenient conditions for the energy production, in terms of economy, concerning the hybrid system can be acquired without a wind turbine and with the ratio between surface area of photovoltaic panel 
[image: image27.wmf](

)

2

m

and average daily consumption 
[image: image28.wmf](

)

kWh

 in amount of 
[image: image29.wmf]5

.

2

=

load

S

E

A

 (related on polycrystalline module application). Autonomous system with 1 day accumulation is in optimal combination desirable to be added a wind component because in that scenario the nonlinearity in supply with the energy is somewhat moderated. The analyzed combination of ratio between the panel surface area and active surface area of the wind turbine 
[image: image30.wmf]14

.

4

=

W

S

A

A

 according to result of optimization and the price of acquired energy is reasonably close to the optimal.

The most favorable conditions of energy production regarding the grid connected system are achieved without a wind turbine present in the system. In case of higher output powers it is possible to appear the necessity for additional transforming of the energy on higher voltage level which makes optimal configuration dependent on expenses of installing electric long distance line and matching transformer, which was not taken into consideration in this particular case. In case of very short distances of the system the ratio between surface area of the photovoltaic panel 
[image: image31.wmf](

)

2

,

m

A

S

 and average daily consumption of the energy 
[image: image32.wmf](

)

kWh

E

load

,

 in amount of  
[image: image33.wmf]5

=

load

S

E

A

 was included inside the optimization which was chosen as economically justified and optimal configuration for Banja Luka region.
REFERENCES 

[1] Mathew, S., (2006). Wind Energy. Springer-Verlag, London.
[2] Duffie, J., Beckman, W., (1980). Solar Engineering of Thermal Processes. John Wiley & Sons Inc. New York.
[3] Sen, Z., (2008). Solar Energy Fundamentals and Modeling Techniques. Springer-Verlag, London.
[4] Republički hidrometeorološki zavod Republike Srpske, (2000). Meteorološko-klimatološke podloge za studiju „TE-TO Banja Luka“, Sveska 1, Banja Luka .
[5] Dumonjić-Milovanović, Svetlana, (2013), Magistarski rad (u proceduri), Univerzitet u Banjoj Luci, Mašinski fakultet Banja Luka.
LOGO WILL BE HERE








�Dipl.-Ing,Svetlana Dumonjić-Milovanović, Banja Luka, Partner Engineering LLC, (svetlanadm@ymail.com) 


�Associate Professor, Petar Gvero, Banja Luka, Faculty of Mechanical Engineering, (gvero.petar@gmail.com) 





6
5

_1427614439.unknown

_1427703870.unknown

_1427791481.unknown

_1427791532.unknown

_1427790263.unknown

_1427616204.unknown

_1427703734.unknown

_1427703742.unknown

_1427703773.unknown

_1427616256.unknown

_1427616054.unknown

_1427616074.unknown

_1427616082.unknown

_1427616089.unknown

_1427616066.unknown

_1427614527.unknown

_1427612665.unknown

_1427613988.unknown

_1427614052.unknown

_1427614177.unknown

_1427614010.unknown

_1427612673.unknown

_1427612655.unknown

_1427612661.unknown

_1427612637.unknown

_1427612633.unknown

