Vesna Ranković, Milorad Bojić, Aleksandar Novaković, Marko Miletić

Building controller synthesis based on the use of MLE+ co-simulation tool

[image: image1.jpg]



Building controller synthesis based on the use of MLE+ co-simulation tool
Vesna Ranković
, Milorad  Bojić
, Aleksandar Novaković
, Marko Miletić
, Nenad Kostić

Summary: Building simulation tools for simulation of the system model and tools to design, evaluate and develop modern control techniques and 
methods play an important role in the design of energy-efficient buildings. Energyplus can accurately simulate actual building performance and energy consumption but its capabilities are insufficient for advanced control system 
design. Both conventional and advanced building control architectures can be implemented using Matlab software. In this paper it is implemented a controller in Matlab that exchanges data with EnergyPlus via MLE+ co-simulation tool.

Key words: Matlab, Energyplus, MLE+, Shading control
1. INTRODUCTION
Building simulation tools like EnergyPlus [1] is a very useful tool to investigate behavior of buildings and for evaluating their energy efficiency and sustainability. This software allows using schedule input of the parameters that affect on the thermal behavior of buildings, such as lighting, electrical equipment, the presence of people in the house, etc. This software also takes into account external influences to buildings such as solar radiation, shading, infiltration, wind direction, etc. Although EnergyPlus simulation tool can accurately simulate energy consumption of a building, its capabilities for modern control design and optimization are inadequate. A popular tool for building energy co-simulation is the Building Controls Virtual Test Bed [2], but it has a few limitations [3]. MLE+ [4] is an open-source Matlab/Simulink toolbox for building energy simulation and control development and validation. The MLE+ is applied to the optimal supervisory control problem of heating, ventilation, and air conditioning systems, [5]. The co-simulation platform MLE+ is introduced to implement an intelligent resilient control strategy in [6].

Shading control example used in this study already exists within MLE+ [7]. In this paper it is proposed controller to control the window shade deployment such that the transmitted solar radiation through the window never exceeds a certain threshold.
2. Building controller synthesis
2.1 Coupling control and building simulation
The analyzed building consists of three zones, Fig.1. The large window equipped with blinds/shades is located at the West zone of the building. The window is exposed to strong solar radiation during the day.
The goal is to control the window shade deployment of the west zone such that the transmitted solar radiation through the window never exceeds a certain threshold. The window blinds is controlled using shading deployment status and shade angle schedule. Design a controller in MLE+ monitors the angle and intensity of the solar radiation incident.  The blinds will be deployed and the shade angle will be set to reduce the possibility of glare when the incident solar radiation exceeds a certain threshold (90 [W/m2]) and the sensible cooling rate exceeds a value of 1300 [W]. 

The EnergyPlus model of the building becomes Matlab S-function using MLE+. A co-simulation platform shown in Figure 2 connecting Matlab and EnergyPlus is used for the control of the shading deployment status (ShadeStatus) and shade angle schedule (ShadeAngle). Input variables of the proposed controller are the angle of the solar radiation incident (IncidentAngle) and intensity of the solar radiation incident (Zone_West_Solar) and the sensible cooling rate (Zone_Sensible_Cool_Rate).
[image: image2.png]&) © O oo




Fig. 1  Analyzed building.
[image: image3.jpg]Control Data-

Shading deployment status

Shade angle schedulel I
| |

MATLAB

—
-

i MLE+ EnergyPlus
I

___| Sensor Data-

Angle of the solar radiation incident
Incident solar radiation
Sensible cooling rate




Fig. 2 Closed-loop control using Matlab and EnergyPlus

Matlab code of the proposed controller is:
if   Zone_West_Solar > 90 && Zone_Sensible_Cool_Rate>1300 
         % SHADES DEPLOYED
        ShadeStatus =userdata.Shade_Status_Exterior_Blind_On ;
        ShadeAngle = IncidentAngle;    
    else
        % SHADES NOT DEPLOYED
        ShadeStatus = userdata.Shade_Status_Off;
        ShadeAngle = 90;
    end    
    % FEEDBACK
    eplus_in_curr.ShadeStatus = ShadeStatus; 
    eplus_in_curr.ShadeAngle = ShadeAngle;
2.2 Simulation results
Chicago design day weather conditions were used.  Those conditions are as follows:

Location: CHICAGO-OHARE

Latitude: 41.98 deg

Longitude: -87.9 deg

Time Zone: -6.0
Elevation: 201.0 m
Annual Heating 99% Design Conditions DB

-17.3    Maximum Dry-Bulb Temperature {C}

0.0       Daily Temperature Range {deltaC}

99063. Barometric Pressure {Pa}

4.9       Wind Speed {m/s}

270     Wind Direction {deg}

0.0      Sky Clearness

21       Day Of Month

1         Month

Annual Cooling 1% Design Conditions DB/MCWB

31.5     Maximum Dry-Bulb Temperature {C}

10.7     Daily Temperature Range {deltaC}

23.0     Humidity Indicating Conditions (wet-bulb) at Max Dry-Bulb

99063. Barometric Pressure {Pa}

5.3        Wind Speed {m/s}

230       Wind Direction {deg}

1.0        Sky Clearness

21         Day Of Month

7           Month
The controller to control the window shade deployment was implemented in Matlab and interfaced with the building energy simulation in EnergyPlus. The input variables of the controller are shown in Fig. 3 and Fig.4. The output variables of the controller are shown in Fig. 5 and Fig.6. The shades are deployed whenever the incident solar radiation exceeds a certain threshold 90 [W/m2]) and the sensible cooling rate exceeds a value of 1300 [W]. 
3. CONCLUSION 


Co-simulation platform with MATLAB and EnergyPlus is used to implement the proposed control strategy. The MLE+ takes advantage of the MATLAB to design and simulate conventional and advanced control architectures. In this paper it is proposed simple controller to control the window shade deployment such that the transmitted solar radiation through the window never exceeds a certain threshold. The building consists of many dynamic subsystems which have mostly non-linear behaviors. Future work will focus on the use of the MLE+ to control of the dynamic subsystems
[image: image4.png]6000

5000

4000

3000

2000

Zone/Sys Sensible Cooling Rate [W]

o
(@)
Q
o

20

40

60
Hour [h]

120




Fig. 3 The sensible cooling rate.
[image: image5.png]Window incident radiation [W/m2]

300

250

200

150

100

il

Hour [h]

800

|
1000

1200




Fig. 4 The incident solar radiation.

[image: image6.png]1.20

Gb 80
Hour [h]

Z
(@)
shiels swAhojdeq Buipeys

OF0




Fig. 5 Shading deployment status

[image: image7.png]40 60
Hour [h]

|

1
1.00

1.20

105

100

Yol
(o]

[o] sifuy speus

90

850




Fig. 6 Shade angle.
ACKNOWLEDGMENT: Research presented in this paper was supported by Ministry of Science and Technological Development of Republic of Serbia, Grants TR 33015 and III 42006.
LITERATURE 
[1] Crawley, D.B., Lawrie, L.K., Pedersen, C.O., Winkelmann, F.C. (2000). Energy plus: energy simulation program. ASHRAE journal, vol. 42, no. 4. p. 49 –56.
[2] Wetter, M. (2011). Co-simulation of building energy and control systems with the building controls virtual test bed. Journal of Building Performance Simulation, vol. 4, no. 3, p. 185–203.

[3] Bernal, W., Behl, M., Nghiem, T.X., Mangharam, R. (2012). MLE+: A Tool for Integrated Design and Deployment of Energy Efficient Building Controls. Proceeding BuildSys '12 Proceedings of the Fourth ACM Workshop on Embedded Sensing Systems for Energy-Efficiency in Buildings. p. 215-216.
[4] Nghiem, T.X. A Matlab-EnergyPlus Co-simulation Interface, http://www.seas.upenn.edu/~nghiem/mleplus.html
[5] Nghiem, T.X., Pappas, G.J. (2011). Receding-horizon Supervisory Control of Green Buildings, 2011 American Control Conference, p. 4416 – 4421. 
[6] Ji, K, Lu, Y., Liao, L., Song, Z., Wei, D. Prognostics enabled resilient control for model-based building automation systems. Proceedings of Building Simulation 2011: 12th Conference of International Building Performance Simulation Association, p. 286-293.
[7] MLE+ Getting Started and Tutorial,mLab Department of Electrical and Systems Engineering University of Pennsylvania, 2012. 
HERE WILL BE LOGO 








� Ph.D., Vesna Ranković, Kragujevac, Faculty of Engineering, University of Kragujevac, (vesnar@kg.ac.rs)


�Ph.D., Milorad  Bojić, Kragujevac, Faculty of Engineering, University of Kragujevac, (milorad.bojic@gmail.com)


�PhD Student, Aleksandar Novaković, Faculty of Engineering, University of Kragujevac, (nbalex00@gmail.com)


4PhD Student, Marko Miletić, Faculty of Engineering, University of Kragujevac, (marko.m.miletic@hotmail.com)


5PhD Student, Nenad Kostić, Faculty of Engineering, University of Kragujevac, (nkostic@kg.ac.rs)





2
3

