Modeling of the building thermal behaviour using nonlinear system identification
Vesna Ranković, Milorad Bojić, Jasna Radulović, Danijela Nikolić, Jasmina Slerlić

[image: image1.jpg]



MODELING OF THE BUILDING THERMAL BEHAVIOUR USING NONLINEAR SYSTEM IDENTIFICATION
Vesna Ranković
, Milorad  Bojić
, Jasna Radulović
, Danijela Nikolić
, Jasmina Skerlić

Summary: Model-based predictive control is a very modern powerful control strategy that uses a model of the plant to predict its future behaviour and has been in focus of researchers in the area of buildings energy management. The aim of this paper is to develop and analyze NARX (Nonlinear AutoRegressive with eXogenous inputs) structure for the modeling of the building thermal behavior. A database was generated using simulation in EnergyPlus software. The NARX identification model was designed using the MATLAB System Identification Toolbox. The input variables analyzed in this paper are: outdoor temperature, heating or cooling power, and direct solar radiation. Simulation results demonstrate that the proposed nonlinear structure can be effective identification tool for development of nonlinear buildings predictive control.
Key words: building, NARX, identification, thermal behaviour
1. INTRODUCTION
Model predictive control (MPC) has been in focus of researchers in the area of buildings [1]. Model predictive control denotes a wide range of control techniques which apply a model to the prediction of future system behavior and calculate the control signals through the optimization of the objective function. The basic conditions that each model should satisfy are practical simplicity, well estimated system dynamics and satisfactory prediction properties.
Various deterministic approaches which uses knowledge of the structure and

physical and material properties of a building and statistical procedures have been applied in order to derive a total model for the heat dynamics of a building. Deterministic models are based on energy and mass balance integral–differential equations and development of such type of model is a very time consuming task.
Prívara et al. [2] proposed a new methodology to obtain a model combining the building energy performance simulation tools and statistical identiﬁcation. Bacher and Madsen [3] applied the procedure for identiﬁcation of the most suitable grey-box models for the heat dynamics of a building on the basis of data from an experiment and prior physical knowledge of the system. Also, the grey box modelling method has been applied to derive a total model for the heat dynamics of a building by Andersen et al. [4]. Jiménez et al. [5] have been presented the application of the MATLAB System Identiﬁcation toolbox to estimate the thermal properties of building components from outdoor dynamic testing, imposing appropriate physical constraints and assuming ARMAX parametric models. The nonlinear black-box models perform better than linear models (ARX, ARMAX) in predicting buildings thermal behaviour [6–9].
The present paper suggests a procedure for identiﬁcation and development NARX structure for the modeling of the building thermal behaviour. A database has been generated using simulation in EnergyPlus software.
2. METHODS FOR NONLINEAR SYSTEMS IDENTIFICATION
 Different methods have been developed in the literature for linear system identification. These methods use a parameterized model. The parameters are updated to minimize an output identification error.

The linear dynamic systems with an input 
[image: image2.wmf]u

 and an output 
[image: image3.wmf]y

 can be described by the ARX (Auto Regresive eXogenous) model:

    
[image: image4.wmf](

)

(

)

(

)

TT

ykkk

==

jqqj

                                            (1)
where:  
[image: image5.wmf](

)

yk

 is the output of the model, 
[image: image6.wmf](

)

k

j

 is the regression vector and 
[image: image7.wmf]q

 is the parameter vector.

The regression vector ARX structure is: 
[image: image8.wmf](

)

(

)

(

)

(

)

(

)

{

(

)

(

)

(

)

(

)

(

)

}

1,2,3,...,

,1,2,3,...

T

a

b

kykykykykn

ukukukukukn

j

=--------

----

 

and the parameter vector is 
[image: image9.wmf]{

}

12123

,,...,,,,,...,

ab

T

nn

aaabbbb

=

q

.

A wide class of nonlinear dynamic systems can be described by the Nonlinear ARX model:


[image: image10.wmf](

)

(

)

(

)

,

ykfk

=

jq

                                                    (2)
where: 
[image: image11.wmf]f

is a nonlinear function whose Inputs are the model regressors.
This block diagram of a nonlinear ARX model is shown in Fig.1.
The nonlinearity estimator block is combine with linear and nonlinear function in parallel and maps the regressors to the model output:

[image: image12.wmf](

)

(

)

(

)

(

)

=-++-

T

fLmrgQm

jjj

                                          (3)
d is a scalar offset, m is the mean of the regressors, Q is a projection matrix.

[image: image13.png]Nonlinearity Estimator

Noniinear|
Regressors Function

Linear
Function

v





Fig. 1 Structure of Nonlinear ARX Models.
The wavelet network can be trained to approximate function 
[image: image14.wmf]g

 as:


[image: image15.wmf](

)

(

)

(

)

akbg

=

=-

å

1

n

kkk

i

g

jj

                                          (4)
where: 
[image: image16.wmf](

)

k

*

 is the wavelet function, n is the number of nonlinear units and 
[image: image17.wmf]a

k

, 
[image: image18.wmf]b

k

 and 
[image: image19.wmf]g

k

 are constant.
3.  Building simulation
The analyzed building consists of three zones, Fig.2.

Basic file description:  1 story building divided into 3 interior conditioned zones. Roof with no plenum. No ground contact with floor. Floor Area: 130.1 [image: image21.wmf]2

m

 
. There is a single window in the west zone south wall. An electric low temperature radiant system is used for heating the ﬂoor of each zone, with power ratings of 12 kW, 8 kW and 8 kW for the north, west and east zones respectively. The ambient air temperature proﬁle was of Chicago, IL, USA. The disturbances due to internal heat gain and solar heat gain were different for every zone and time-varying.


In this case study, we used the EnergyPlus model as the ground truth for the building, i.e., it was considered as the “real” building. The program EnergyPlus 6.0 is used, which allows the simulation of thermal behavior of buildings during the analyzed period. 
4. Simulation results

In this work, NARX (Nonlinear AutoRegressive with eXogenous inputs) structure are chosen to predict zone temperature (North, West and East). The procedure for determining proper NARX models from EnergyPlus data involves three steps: (1) obtaining input-output data by simulating (2) model structure selection (train NARX with different delays), and (3) model validation. The input vector of the considered models is: 

[image: image22.wmf][

]

T

ehc

=TPR

u


where:
[image: image23.wmf]e

T

 is outdoor temperature, 
[image: image24.wmf]hc

P

 denote heating or cooling power and
[image: image25.wmf]R

 is direct solar radiation.
[image: image26.png]2one pescription Details:

€0,12.192,0) (9.144,12.192,0)

North

(6. 096, 6. 096, 00
(12.192,6. 069, 0)

(0,6.096,0) } (5.144,6.096, 0)
1 1
west } East } window = ¥
|
|
s __| |

€0,0,0) (6.069,0,0) (12.192,0,0)




Fig. 2 The analyzed building.
The number of the NARX inputs is determined by the input and output lags. In this paper, the satisfactory accuracy is obtained for regression vector: 

[image: image27.wmf](

)

(

)

{

}

j

=----

1,(1),(1),(1)

T

iehc

kTkTkPkRk

                 (5)
The numbers of units wavelets estimator have been automatically chosen by the estimation algorithm. This section presents the results of simulations for the west zone. 
The wavelets estimator for prediction WEST zone temperature has 94 units.
The time series of the inputs and output variables are shown in Fig. 3, Fig. 4, Fig. 5 and Fig. 6. 
[image: image28.png]Te [0C]

-10

12

24

36

48
Time [h]

60

72

84

96




Fig. 3 The outdoor temperature.

[image: image29.png]® © < o~ o°
EEEEEE




Fig. 4 The power heating or cooling.

[image: image30.png]0.6

R [KW/m2]
o
~

o
[N}





Fig. 5 The direct solar radiation.
[image: image31.png]—Ti- EnergyPlus
—Ti-NARX predicted

A

48
Time [h]




Fig. 6 The indoor temperature.

5. CONCLUSION 
In this paper, a procedure for using MATLAB System Identification Toolbox for modeling building thermal behaviour is proposed. Nonlinear ARX model is more suitable than the linear estimator because room temperatures is governed by nonlinear equation.The result of the simulation show that NARX model predicted values are in accordance with the values obtained by the simulation.
The future research should Include the application of the proposed technique on a real input–output data collection from measurements.

ACKNOWLEDGMENT: Research presented in this paper was supported by Ministry of Science and Technological Development of Republic of Serbia, Grants TR 33015 and III 42006.
LITERATURE 
[1] Freire, R., Oliveira, G., Mendes, N. (2008). Predictive controllers for thermal comfort optimization an energy savings, Energy and Buildings, vol. 40, no. 7, p. 1353–1365. 

[2] Prívara, S., Cigler, J., Váňa Z., Oldewurtel, F., Sagerschnig C., Žáčeková, E. (2013). Building modelling as a crucial part for building predictive control, Energy a Buildings vol. 56, p. 8–22. 

[3] Bacher, P., Madsen, H. (2011). Identifying suitable models for the heat dynamics of buildings. Energy and Buildings, vol. 43, no. 7, p. 1511–1522.

[4] Andersen , K.K,  Madsen, H., Hansen, L.H. (2000). Modelling the heat dynamics of a building using stochastic differential equations. Energy and Buildings, vol. 31, no. 1, p. 13–24.

[5] Jiménez, M.J., Madsen, H., Andersen, K.K. (2008). Identiﬁcation of the main thermal characteristics of building components using MATLAB. Building and Environment, vol. 43, no. 2, p. 170–180.
[6] Mechaqrane, A., Zouak, M. (2004). A comparison of linear and neural network ARX models applied to a prediction of the indoor temperature of a building. Neural Computing & Applications, vol. 13, no. 1, p. 32–37.

[7] Ruano, A.E., Crispim, E.M., Coincecao, E.Z.E., Lucio, M.M.J.R. (2006).  Predictions of building’s temperature using neural networks models. Energy and Buildings, vol. 38, no. 6, p. 682–694.
[8] Patil, S.L., Tantau, H.J., Salokhe, V.M. (2008). Modelling of tropical greenhouse temperature by autoregressive and neural network models. Biosystems Engineering, vol. 99, no. 3, p. 423–431.
[9] Mustafaraj, G., Lowry, G., Chen, J. (2011). Prediction of room temperature and relative humidity by autoregressive linear and nonlinear neural network models for an open office. Energy and Buildings,  vol. 43, no. 6, p. 1452–1460.

HERE WILL BE LOGO 








� Ph.D., Vesna Ranković, Kragujevac, Faculty of Engineering, University of Kragujevac, (vesnar@kg.ac.rs)


�Ph.D., Milorad  Bojić, Kragujevac, Faculty of Engineering, University of Kragujevac, (milorad.bojic@gmail.com)


�Ph.D., Jasna Radulović, Faculty of Engineering, University of Kragujevac, (jasna@kg.ac.rs)


4Assistant, Danijela Nikolić, Faculty of Engineering, University of Kragujevac, (� HYPERLINK "mailto:danijelan@kg.ac.rs" �danijelan@kg.ac.rs�)


5Researcher, Jasmina Skerlić, Faculty of Engineering, University of Kragujevac, (� HYPERLINK "mailto:jskerlic@gmail.com" �jskerlic@gmail.com�)





6
5

_1492516913.unknown

_1492527742.unknown

_1492528692.unknown

_1492605405.unknown

_1492605423.unknown

_1492632415.unknown

_1492605414.unknown

_1492605352.unknown

_1492528658.unknown

_1492528676.unknown

_1492527865.unknown

_1492525676.unknown

_1492527643.unknown

_1492517368.unknown

_1492516039.unknown

_1492516342.unknown

_1492516481.unknown

_1492516173.unknown

_1492515255.unknown

_1492516009.unknown

_1460324136.unknown

_1492515208.unknown

_1203150193.unknown

