Mića Vukić, Velimir Stefanović, Predrag Živković, Mirko Dobrnjac
Experimental Investigation of Thermal and Flow Processes in Shell And Tube Heat Ehchangers

[image: image1.jpg]



EXPERIMENTAL INVESTIGATION OF THERMAL AND FLOW PROCESSES IN SHELL AND TUBE HEAT EHCHANGERS
Mića Vukić 
, Velimir Stefanović 
, Predrag Živković 
, Mirko Dobrnjac 

Abstract: Experimental investigations were done to identify influence of thermal and flow quantities and shell side geometry to STHE’s heat exchange intensity. In this paper special attention was made to number of segmental baffles (with baffle cut of 22%) influence on apparatus efficiency investigation.

Keywords: Shell and tube heat exchanger, experimental research, number of baffles
EKSPERIMENTALNO ISTRAŽIVANJE TERMO STRUJNIH PROCESA U DOBOŠASTIM IZMENJIVAČIMA TOPLOTE
Rezime: Eksperimentalna istraživanja sprovedena su u cilju utvrđivanja uticaja termo-strujnih veličina i geometrije izmenjivača toplote na intenzitet razmene toplote. U ovom radu posebna pažnja posvećena je istraživanju uticaja broja segmentnih pregrada (sa veličinom okna od 22%) na toplotnu efikasnost aparata.
Ključne riječi: Dobošasti izmenjivač toplote, eksperimentalno istraživanje, broj pregrada
1. Introduction remarks
Shell and tube heat exchangers (STHE’s) are apparatuses in which the heat exchange between hoter and colder fluid is performing. Fluid flowing through tubes is called – tube fluid, and fluid flowing around tube bundle is called – shell side fluid. Baffles, placed in shell side space, are providing the cross flow direction of shell side fluid and so the more intensive heat exchange between fluids could be realized. Besides, baffles are carriers of tube bundle, which helps them to decrease the deflection in horizontal and vibrations in horizontal and vertical apparatuses. STHE’s usually have combined fluid flow, which means that there is parallel in one, and counterflow in other part of the exchanger. This apparatuses are usually denoted as m-n STHE’s, where m is the number of fluid passes through the shell, and n is the number of fluid passes through the tube bundle. If the STHE is with so called „full tube bundle“, the shell side fluid flows through baffle cuts along the tubes. On the shellside, there is not just one stream, beside a main cross-flow stream the four leakage or bypass streams exist as a result of design – type – baffle to tubes, baffle to shell and tube bundle to shell gaps (tube – to – baffle hole leakage stream, bundle bypass stream, pass – partition bypass stream and baffle – to – shell leakage stream).

One of STHE manufacturer’s main causes is to improve their exploitation reliability and efficiency. Two approaches in STHE design improve are possible: experimental investigation, which is very expensive and long – lasting, because of shell side complex geometry, and numerical investigations. Numerical simulations can be used to check the old and to develop new, more efficient STHE design. Shellside flow is almost always turbulent since tube bundle and baffles are very nice turbulent promoters. Character of flow around some tube rows in tube bundle is strongly influenced by tube layout (square, rotated square, triangular, rotated triangular, circular).
Character of flow around the tubes has a direct influence on heat exchange between fluids. Problem is more complex if heat transfer is simultaneous with phase change. Since the detailed measurements of turbulent characteristics of shellside fluid flow are almost impossible, the calculated fields of pressure, velocity, temperature as well as turbulent characteristics are of great significance in explaining very complex thermal and flow processes in STHE’s.
Basically, one can conclude that heat transfer between fluids in STHE’s is highly influenced not only by thermal and flow quantities, such as inlet temperatures and velocities, but also with baffle cut size, baffle spacing, size of inlet and outlet zones and number of baffles [1 - 8]. To investigate influence of mentioned parameters, thermal, flow and geometric, with other words, to find the „apparatus response“to thermal and fluid quantities and shell sidegeometry, in steady regime, by experimental and numerical methods, it was necessary to concept one compact experimental STHE.

In this paper, special attention was made to experimental investigation of segmental baffles number (with baffle cut of 22%) to STHE efficiency.

2. Experimental investigation
Experimental STHE, tupe 1-2U, was projected and manufactured in cooperation with firm MIN Inzinjering from Nis. Measuring place was formed in the boiler house of the Mechanical Faculty in Nis. Experimental installation is shown on Photograph 1. Basic part of the installation is STHE, type 1-2U, which is shown on the Photograph 2. Tube bundle is made of copper U-pipes, Φ15/13 mm, with rotated triangular tube layout and tube pitch of 21mm. There are 48 tubes in the tube bundle. STHE’s active area for heat exchange is 1.8 m2. Shell is made of carbon steel, Φ193.7/182.9 mm. STHE’s full length is 1217 mm. Taps for pressure drop measurements are set up on the shell, along with openings for thermocouple carriers. Three packages of segmental baffles with baffle cuts of 22%, 27% and 32% are located in the shell. There are 5 segmental baffles in every package. Segmental baffles and horizontal baffle are made of copper. Two measuring paths with impurity catchers, measuring diaphragms and TA-STAD valves are made. There are long enough rectilinear pipe sections before and after the diaphragms in order to stabilize the water flow. Water flow regulation is done with valves. Heating of water up to certain temperature is done with four electrical boilers, with 30kW strength. Water temperature adjustment is provided with calotrons, as well as with one of the boilers heaters regulation of strength. The heating fluid is warm water, and the heated is cooling water from the local water supply. Flowing of the heating fluid through the shell is done by circulation pump.
[image: image2.jpg]



Photograph 1
Experimental installation

[image: image3.jpg]



Photograph 2
Experimental shell and tube heat exchanger

Experimental investigation is done in conditions of the summer ambient conditions in the period May-September. In all experiments constant heating fluid flow (9m3/h), as well as inlet STHE’s heated fluid (15°C) temperature was maintained. Heated fluid flow rate (3m3/h, 4m3/h, 5m3/h) and temperature (50°C, 60°C) were varied at the inlet. At the beginning series of experiments without baffles in the shell were done. After that, baffles were set into the shell (one, two, three, four and five baffles). Six experiments were done for every geometry change.

3. Measurements results
Heating and heated fluid flow rate measurements were done with standard measuring diaphragms, as well as with pressure drop measurements on TA-STAD valves with CBI acquisition system (Computerized Balancing Instrument).

Pressure in the closed circulation heating fluid circle (primer) was measured with laboratory mechanical manometer. In all experiments manometer indicatons was in the range 3 – 3.5 bar.

Pressure drop in the STHE’s tube bundle and on the measuring diaphragms were done with the hydrostatic manometer (U-pipe with mercury). In the measurements done average tube bundle pressure drop was 3710 Pa.

STHE’s shell side pressure drops were measured by specially made system consisting of taps set up on the shell, transparent rubber hoses, collector with 16 connexions, valves, shanks, millimeter partitioned scale and hand pump.System is shown on the photography 2.1. All taps from the STHE’s shell are connected by transparent rubber hoses into a collector (totally 15 branches). One side of the collector is closed, and the other side is connected to the compressed air source through a valve. After desired heated fluid flow compressed air is was insufflated into the collector, which caused forming of adequate high water columns. This way shell side pressure drop, as well as pressure drop along STHE’s shell, i.e. pressure drop between two baffles and pressure drop in the baffle cut.

During each experiment, after accomplishing steady state heat exchange regime (which was accomplished after 25-30 min. in expreiments done), fluid temperature are measured with 16 previously calibrated chromel-allumel thermocouples of 0.2 mm diameter, using the Hewlett-Packard acquisition system. Cold sides of all thermocouple were sunk into insulated tank filled with 1:2 water and ice mixture. All thermocouples were set into so called thermocouple „movable platforms“. Apparatus inlet and outlet, heating and heated fluid temperatures (five thermocouples), as the heating fluid temperatures in the central shell’s plane and 5 mm from the shell wall, on eleven formerly defined locations along the STHE were measured. Heated fluid inlet temperatures in the beginning, and outlet temperatures in the end of the experiment were controlled with a mercury thermometer. This thermometer was also used for ambient temperature measurements.

Measuring results are showed in the form of diagrams. On the x-axis measuring place position is shown, and temperature value on the y-axis.

Figure 1 shows heating fluid temperature change along the STHE’s axis and on 5mm from the shell wall for one work regime. Figure 2 shows heating fluid temperature change in the STHE’s axis depending on the flow rate. Figure 3 show heating fluid temperature change along the STHE’s axis depending on the segmental baffles number. Figure 4 shows the apparatus heat efficiency increase depending on the segmental baffles number, comparing with the case with no baffles.
[image: image4.png]TEMPERATURE [°C]

70

60 fx

50

&

40

$4

ol

30

20

10

100

200 300 400
MEASURING PLACE[mm]

®axis A5mm from wall

500

600




  [image: image5.png]TEMPERATURE [°C]

70

60

50

40

30

20

10

o> m

ta

*
*

100 200

300

400 500

MEASURING PLACE[mm]

oVt=3m3/h

AVt=4m3/h

mVt=5m3/h

600





	Fig. 1
Heating fluid temperature change along the STHE’s axis and on 5 mm from the shell wall for: Vt, = 4 m3/h, Np = 1,    BC = 22%, t1t = 60oC
	Fig. 2
Heating fluid temperature change along the STHE’s axis depending on the flow rate for: Np = 1, BC = 22%, t1t = 60oC


[image: image6.png]70 -

2l
o e
o ma
T %
¢ |De
<
e
a4 @
a0 m
«e
g
o o =) o =)
@ c) < @ (3

[0d38NLYYIdNEL

300 400 500 600
MEASURING PLACE[mm]

200

100

=5

oNp

=3

BNp

ANp=1

=0

©Np




  [image: image7.png]W

HEAT EFFICIENCY INCREASE [%]

-
N

-
o

o]

1 2 3 4
NUMBER OF BAFFLES

oVt=3m3/h mMVt=4m3/h AVt=5m3/h





	Fig. 3
Heating fluid temperature change along the STHE’s axis depending on the segmental baffles number for:                 Vt, = 5 m3/h, BC = 22%, t1t = 60oC
	Fig. 4
Apparatus heat efficiency increase depending on the segmental baffles number, comparing with the case with no baffles, for t1t = 50oC


4. Discussion of the results
Results of the experiments done shows that STHE’s heat excange strongly depends of the shell side geometry (number of segmental baffles, baffle cut size, baffle distance, the first and the last baffle position to inlet and outlet nozzle, respectively, size of the constructive clearances).

With the experimental results analysis the following can be concluded:

· Shell side baffle strongly influence the fluid flow characteristics and cause vortex appearance (downstream behind the baffle);

· Downstream fluid temperatures are significantly lower (up to 100C behind the first baffle) which is caused by intensive heat exchange in the cross flow ahead and before the baffle, and by axial flow in the baffle cut. Certainly, this is also caused by baffle to shell leaking, and by cooling of the fluid through the shell wall;

· Increasing of heating fluid flow rate decreases temperature drops behind the baffle;

· Increasing of the heating fluid inlet temperature, and/or flow rate maintains temperature change character in the axis and near the shell wall;

· The most intensive heat exchange is in the STHE’s inlet zone (to the first baffle)

· Heating fluid temperature near the shell wall is lower, compared to the heating fluid temperature in the STHE’s axis, up to the first baffle, and after the first baffle situation is reversed, which is consequence of the baffle to shell leaking, because it doesn’t take place in the heat exchange;

· Influence of this leaking increases downstream the first baffle;

· Increase of segmental baffles number has higher influence to the STHE’s heat efficiency than the increase of the heating fluid flow rate;

· In this case (Vt = 5 m3/h, t1t = 50oC), with five segmental baffles STHE’s heat efficiency increased for 9.4%.

LITERATURA
[1] Aicher, T., Kim, W., Experimental Investigation of the Influence of the Cross Flow in Nozzle Region on the Shell Side Heat Transfer in Double-Pipe Heat Exchangers, Int. Comm. Heat and Mass Transfer, Vol. 25, No. 1, pp. 43-58, 1998.

[2] Gaddis, E., Gnielinski, V., Pressure Drop on the Shell Side of Shell-and-Tube Heat Exchangers with Segmental Baffles, Chemical Engineering and Processing 36, pp. 149-159, 1997.

[3] Gay, B., Mackley, N., Jenkins, J., Shell-Side Heat Transfer Coefficients in Cylindrical Heat Exchangers the Influence of Geometrical Factors. II –– The Leakage Case, Letters in Heat and Mass Transfer, Vol. 8, Iss. 6 , pp. 437-452, 1981.

[4] Ilić, G., Vukić, M., Vučković, G., Parameters Influencing the Effective and Optimal Design of Shell and Tube Heat Exchangers, International DAAD Seminar, 27-29.11.2000.god., Sofia, Bulgaria.

[5] Li, H., Kottke, V., Effect of Baffle Spacing on Pressure Drop and Local Heat Transfer in Shell-and-Tube Heat Exchangers for Staggered Tube Arrangement, International Journal of Heat and Mass Transfer, Vol. 41, No. 10, pp. 1303-1311, 1998.

[6] Mukherjee, R., Effectively Design Shell and Tube Heat Exchangers, Chemical Engineering Progress, 1998.

[7] Vukić, M., Eksperimentalno i numeričko istraživanje termo-strujnih procesa u dobošastim razmenjivačima toplote, Doktorska disertacija, Mašinski fakultet Univerziteta u Nišu, Niš, 2004.

[8] Sparrow, E. M.; Reifschneider, L. G., Effect of Interbaffle Spacing on Heat Transfer and Pressure Drop in a Shell-and-Tube Heat Exchanger, International Journal of Heat and Mass Transfer Vol. 29, Iss. 11, pp. 1617-1628, 1986.









� Prof. dr Mića Vukić, Niš, University of Niš, Faculty of Mechanical Engineering in Niš, (micav@masfak.ni.ac.rs)


� Prof. dr Velimir Stefanović, Niš, University of Niš, Faculty of Mechanical Engineering in Niš


� Dr Predrag Živković, Niš, University of Niš, Faculty of Mechanical Engineering in Niš


� Prof dr Mirko Dobrnjac, University of Banja Luka, Faculty of Mechanical Engineering





6
5

