MSc Veselin Blagojević, dr Nebojša Lukić, dr Novak Nikolić, MSc Aleksandar Nešović
Heat recovery of ventilation air in existing educational building in Doboj

[image: image1.jpg]



HEAT RECOVERY OF VENTILATION  AIR  IN EXISTING EDUCATIONAL BUILDING IN DOBOJ 
Veselin Blagojević
, Nebojša Lukić
, Novak Nikolić
, Aleksandar Nešović

Summary: This research is related to the heat recovery of ventilation  air. The analysis includes the heat recovery of air in case when  ventilation  is defined according to the  air changes per hour and according to the current presence of people in ventilated zones. The research was conducted for an existing nonresidential (educational) building in Doboj. The large heat losses through the ventilation system can be reduced by installing a energy recovery ventilator. Analysis of the presence of people in the zones can have a major impact on the operation of the ventilation system and electricity consumption. It is assumed that the dependence of these two factors is very important and that the study could be a starting point for solving this problem in a given area. The analysis was conducted in the software EnergyPlus.
Key words: Heat recovery, ventilation, EnergyPlus, nonresidential building.

1. INTRODUCTION 
The big problem in modern construction of buildings represent requirements for room ventilation and maintaining of hygienic conditions. The solution for this problem is installation of heat recovery ventilation system. In order to reduce energy consumption of ventilation system, utilization of heat from the exhaust air is almost mandatory. However, the problem may represent leakage of heat, which can drastically reduce the efficiency of ventilation and heat recovery. In addition, these systems use electricity, and their improper handling can lead to increase of electricity consumption [1].
This work represents the first steps of implementation of the methodology for calibration of simulation models through definition of parameters that have the most impact on the energy consumption of buildings and end-use of buildings. Sensitivity analysis was applied over the estimated load for the heating and cooling of the building in order to determine more accurate values for the input parameters representing a major impact on the heat load.
The global crisis and greenhouse gases put additional pressure on the energy consumption in buildings. Particular emphasis is on high energy consumption in nonresidential buildings [2].
2. CALIBRATION AND SIMULATION OF BUILDING MODEL 
The investigation was conducted for a existing nonresidential building (educational building), The Faculty of Transport and Traffic Engineering in Doboj (B&H). 
To simulate thermal behavior of this building and have accurate calculation results, software EnergyPlus version 7.1 was used. This program is very useful tool for modeling of energy and environmental behavior of buildings [3]. In the software, it is possible to input how people use building during the space heating and cooling. In  this direction, the complex schedules of heating and cooling can be deﬁned together with schedules for use of lighting, interior equipment and occupancy in the building. The inﬂuence of the solar radiation, shadowing and inﬁltration can be also taken into consideration. The first step in the study was the collection of project documents and definition of the object geometry in the software Google SketchUp version 8. 
[image: image2.png]



Fig. 1 The geometry of the investigated building
2.1 CHARACTERISTICS OF THE BUILDING AND PARAMETERS
The investigated building has 34 zones distributed on 4 levels and total floor (heating) area of 1562.70 m2 (Fig. 1). Since it is a new building, the attention was paid to that the biggest part of the building be oriented toward south in order to maximize solar gains. The percentage of the window area relative to the area of the entire surface of the walls of the building is 32.62%. The value of the parameter SHGC is 0.765. It was assumed that building is not surrounded by any other building. Large windows provide sufficient daylight in the rooms and for this reason the use of lighting in most rooms is only required in the morning and evening. The characteristics of the building constructions are given in Table 1.
Table 1 The characteristics of the building constructions
	Construction
	Layer
	U[W/m2K]

	Window
	Glass (0.4 cm), Air (1.3 cm), Glass (0.4 cm); 
	2.770

	Exterior wall
	Brick (12 cm), Expanded polystyrene foam (15 cm),  Air (2 cm), Clay block (25 cm), Lime mortar (2.5 cm)
	0.225

	Interior wall
	Lime mortar (2.5 cm), Brick (12 cm), Lime mortar (2.5 cm) 
	0.17

	Roof
	Gravel (5 cm), Waterproofing (0.2 cm), Vapor barrier (0.2 cm), Cotton (5 cm),Vapor barrier (0.2 cm), Lightweight concrete (5cm),Cement screed (4cm), Clay block (16cm), Lime mortar (2.5 cm);
	0.566

	Floor with tiles
	Stone (25 cm), Gravel (5 cm), Lightweight concrete  (4 cm), Waterproofing (0.2 cm), Lightweight concrete  (4 cm), Ceramic tile (1.5 cm)
	2.831

	Interior ceiling 

(with tiles)
	Ceramic tile (1.5 cm), Cement screed (4cm), Clay block (16cm), Lime mortar (2.5 cm);
	1.21


Data about lighting and interior equipment were entered in the software on the basis of the current situation. In the whole building the neon lighting is installed. The power of lights is in range of 72W to 504W depending on the surface area. The lights in the hallways and toilets operates from 8 am to 4 pm, in the offices and classrooms from 8 am to 11 am. The power of interior equipment in the hallways ranges from 20W to 1500W. In classrooms it amounts 200W. Maximum power of this equipment in the toilet is 500W. Equipment operation follows user activity in the building. Number of people (users) is defined based on the capacity of the rooms and their purpose, while the occupancy of the rooms is defined based on a schedule of teaching in the winter semester of 2016/17 year. Activity level of people is defined as walking and sitting. The activity level, age, body weight and clothing of people are the factors that present heat gains. Since the majority of users in the building is between the ages of 18 to 30 years, the average heat gain per person for walking (210W) and seating (105W) was adopted [4]. Number of people and their occupancy within the building are very important in this investigation. Therefore, Table 2 gives the data about zone floor area, number of people and their occupancy. 
Table 2 Floor area of the zones, number of people and their occupancy
	Zone
	Area
	People

	
	[m2]
	Num.
	Fractions of people occupancy

	P1
	69.20
	50
	8:45-9:00=1; 9:00-10:00=0.1;  10:00-11:45=1;  11:45-12:00 =0.1; 12:00-13:00=0.1;  13:00-14:50=1;  14:50-17:00=1;

	P4
	43.44
	21
	8:00-9:00=0.8;      9:00-13:00=1;       13:00-14:00=0.8;

	P4a
	43.19
	49
	8:00-9:00=0.8;      9:00-13:00=1;       13:00-14:00=0.8;

	P5
	71.30
	2
	8:00-9:00=0.5;    13:00-14:00=0.5;    14:00-15:00=1;

	P6
	19.55
	2
	8:00-17:00=0.5;

	P7
	42.12
	43
	8:00-13:00=0.5;

	P8
	51.98
	48
	8:00-13:00=0.5;

	P9
	9.31
	2
	8:00-11:00=0.5;    11:00-15:00=1;      15:00-18:00=0.5;

	PS1
	64.19
	50
	8:00-16:00=0.1;

	PS3
	51.98
	48
	9:00-15:00=0.5;

	PS4
	42.12
	29
	9:00-13:00=0.8;    13:00-14:00=0.5;

	PS5
	20.18
	2
	8:00-16:00=1;

	PS6
	18.51
	2
	8:00-16:00=1;

	PS7
	18.77
	2
	8:00-16:00=1;

	PS8
	20.40
	2
	8:00-9:00=1;           9:00-19:00=0.5;

	PS9
	28.86
	2
	8:00-17:00=0.5;

	PS10
	22.56
	2
	8:00-19:00=1;

	PS11
	20.63
	2
	8:00-12:00=0.5;     12:00-13:00=1;     13:00-15:00=0.5; 

	PS12
	20.35
	2
	8:00-19:00=0.5;

	PS13
	22.18
	2
	8:00-11:00=1;        11:00-15:00=0.5;

	DS1
	76.08
	50
	8:00-9:00=0.2;         9:00-15:00=0.1;   15:00-16:00=0.1;

	DS3
	53.39
	43
	8:00-9:00=0.3;         9:00-12:00=0.5;   12:00-13:00=0.3;

	DS4
	118.78
	78
	8:00-12:00=0.3;     12:00-14:00=0.2;

	DS5
	14.66
	2
	8:00-11:00=1,        11:00-16:00=0.5;

	DS6
	15.98
	2
	8:00-15:00=1;        15:00-16:00=0.5;

	DS7
	115.83
	78
	8:00-9:00=0.2;          9:00-11:00=0.3;  11:00-14:00=0.2;

	DS8
	36.23
	2
	8:00-15:00=0.5;

	TS1
	76.08
	80
	8:00-13:00=0.1;      13:00-14:00=0.5;  14:00-16:00=0.01;

	TS3
	53.39
	43
	8:00-10:00=0.3;      10:00-11:00=0.5;  11:00-14:00=0.3;

	TS4
	118.78
	78
	9:00-15:00=0.2,

	TS5
	14.66
	2
	8:00-15:00=1;

	TS6
	15.98
	2
	8:00-15:00=1;

	TS7
	115.83
	78
	8:00-12:00=0.3;

	TS8
	36.23
	2
	8:00-16:00=0.5;

	Total
	1562.70

(Sum)
	902

(Sum)
	


2.2 HEATING SYSTEM 

The heating system consists of a boiler on natural gas, convective baseboard heaters, variable flow pump and heat recovery ventilators. The water convective baseboard heaters and ventilators are put in each of the heated zone. The heating system operates each day of the heating season from 15th of October to 15th of April. During the day, they operates from 7 am to 10 pm, if the room temperature is below 20°C, from 10 pm to 7 am if the room temperature is below 15°C. The heat exchanger of the energy recovery ventilator is activated when the temperature of the outdoor air is below 18°C.  
2.3 SIMULATION SCENARIOS
This investigation is related to the heat recovery of ventilation air of the existing nonresidential building in Doboj. The analysis includes three simulation scenarios: 1 - heating without heat recovery of ventilation air; 2 - heating with heat recovery of ventilation air in case when ventilation is defined according to the air changes per hour; 3 - heating with heat recovery of ventilation air in case when ventilation is defined according to the current presence of people in ventilated zones.
In order to simulate the operation of existing heating system the size of the same is determined by assuming that the ventilation rate is 0.5 1/h. For the scenario 2 the adopted ventilation rates are: 1.5 1/h for offices and toilets and 2 1/h for classrooms [5]. On the other side for scenario 3 the ventilation rate is determined according to the people occupancy. The adopted value for the supply (outdoor) air is 7 m3/h per person [6]. It has to be noted that for all three scenarios it was assumed that air tightness of the thermal building envelope is minimal. In other words, there is no infiltration of outdoor air. The opening of doors and windows is not taken into consideration. 

3. RESULTS
This investigation includes analysis of energy consumption for heating the existing educational building for three proposed scenarios of heating system operation. The values for energy consumption, percentage energy savings and specific energy consumption for all three cases are given in Table 3. Percentage energy savings for scenario 2 and 3, in relation to the scenario 1 are 65.91% and 81.72%, respectively. The obtained values can be explained by the fact that the ventilation heat losses are significantly higher than transmission heat losses. The reason is very low value for U coefficient of the exterior wall as well as the high values of the air changes per hour for the educational nonresidential building defined according to [5]. The energy consumption for scenario 3 is the lowest because the ventilation is defined according to the current presence of people in the zone.
Table 3 The simulation results for three analyzed scenarios
	RESULTS OF RESEARCH

	
	Example 1
	Example 2
	Example 3

	Natural Gas [kWh]

	196430.46
	64753.09
	35545.41

	Electricity:Heating (Fans, Pumps) [kWh]
	3510.41
	3410.71
	1010.44

	Total energy consumption [kWh]

	199940.87
	68163.8
	36555.85

	Specific energy consumption [kWh/m2]
	127.95
	43.62
	23.39

	Percentage energy savings [%]
	-
	65.91
	81.72


4. CONCLUSION
In order to provide energy efficiency in buildings, the heat recovery system of  ventilation air is often installed. The efficiency of this system depends on many factors like duration of the heating season and climatic conditions. In this paper the heating consumption for a existing nonresidential (educational) building for three proposed scenarios of heating system operation was analyzed. Proposed simulation scenarios are: 1 - heating without heat recovery of ventilation air; 2 - heating with heat recovery of ventilation air in case when ventilation is defined according to the air changes per hour and 3 - heating with heat recovery of ventilation air in case when ventilation is defined according to the current presence of people in ventilated zones. The obtained percentage energy savings for scenario 2 and 3, in relation to the scenario 1 are 65.91% and 81.72%, respectively. The reason lies in the fact that the ventilation heat losses are significantly higher than transmission heat losses. The heating consumption for scenario 3 is the lowest because the ventilation is defined according to the current occupancy of people.
ACKNOWLEDGEMENTS: This investigation is а part of project TR 33015 of the Technological Development of the Republic of Serbia. We would like to thank the Ministry of Education, Science and Technological Development of the Republic of Serbia for their financial support during this investigation.
REFERENCES 

[1] ROULET, C.-A., et al., Real heat recovery with air handling units. Energy and Buildings, Vol. 33, No. 5, pp. 495-502, 2001.
[2] Wang, Y., Zhao, F. Y., Kuckelkorn, J., Li, X. H., Wang, H. Q., Indoor air environment and night cooling energy efficiency of a southern German passive public school building operated by the heat recovery air conditioning unit. Energy and Buildings, Vol. 81, pp. 9-17, 2014.
[3] Bojić, M., Nikolić, N., Nikolić, D., Skerlić, J., Miletić, I., A simulation appraisal of performance of different HVAC systems in an office building. Energy and Buildings, Vol. 43, No. 6, pp. 1207-1215, 2011.
[4] Inbar, O., Morris, N., Epstein, Y., Gass, G., Comparison of thermoregulatory responses to exercise in dry heat among prepubertal boys, young adults and older males. Experimental Physiology, Vol. 89, No. 6, pp. 691-700, 2004.
[5] Heating systems in buildings - Method for calculation of the design heat load, SRPS EN 12831, Official Gazette 80/12, 2012.
[6] Regulations on Energy Efficiency of Buildings, Republic of Serbia, Ministry of Environment, Mining and Spatial Planning, Official Gazette 61/11, 2011.
LOGO WILL BE HERE








� MSc Veselin Blagojević, University of Kragujevac, Faculty of Engineering, Serbia,e-mail: veso.doboj@gmail.com


� dr Nebojša Lukić, University of Kragujevac, Faculty of Engineering, Serbia, e-mail: lukic@kg.ac.rs


� dr Novak Nikolić, University of Kragujevac, Faculty of Engineering, Serbia, e-mail: novak.nikolic@kg.ac.rs 


� MSc Aleksandar Nešović, University of Kragujevac, Faculty of Engineering, Serbia, e-mail: aca.nesovic@gmail.com 





2
5

