REDUCING CLIMATE CHANGE BY INSTALLING A NEW PHOTOVOLTAIC POWER PLANT IN BULGARIA
Plamen Tsankov1
1 Technical University of Gabrovo, Faculty of Electrical Engineering and Electronics,
4 Hadji Dimitar str., 5300 Gabrovo, Bulgaria

Summary: A three new roof-mounted 10 kWp grid-connected photovoltaic (PV) power plants have been constructed in the Technology Park at the Technical University of Gabrovo, Bulgaria, as part of a project “Competence Center – Intelligent Mechatronic, Eco and Energy Saving Systems and Technologies”. Three different types of technology of the PV modules have been used: monocrystalline silicon (mono-Si), cadmium telluride (CdTe) and copper indium gallium selenide (CIGS). With the new three power plants, together with the existing photovoltaic power plants in TU-Gabrovo with modules of amorphous silicon and poly-crystalline silicon, 5 different photovoltaic materials can be tested simultaneously. A small 500 Wp mono-Si photovoltaic thermal hybrid solar collectors (PVT) PV system is also constructed. The power plants are equipped with a system for monitoring the meteorological and electrical operating parameters, which measures, displays and stores data on solar radiation, temperature, wind speed, currents, voltages, and electrical power of each power plant. The technical characteristics of the components of the PV plants are given in the paper. Schemes with a basic wiring diagram, disposition of the three PV subsystems on the roof of the building at the technology center are presented. Initial comparative data from software for monitoring of meteorological and electrical operating characteristics of the three different types of PV subsystems are shown. Data on the saved CO2 emissions from the avoided production and transmission of electricity according to the specific ecological equivalent of energy resources and energy for the region of Bulgaria, due to the operation of photovoltaic power plants, are presented.
Keywords: monocrystalline silicon, cadmium telluride, copper indium gallium selenide, grid-connected photovoltaic power plant, monitoring system, meteorological and electrical operating characteristics, smart solar logger, carbon emissions, climate change.  
1.  INTRODUCTION
Exploring the possibilities and technical solutions for influencing climate change using renewable energy sources, and in particular - photovoltaic (PV) systems, is among the most common in contemporary scientific research [1,2,3,4,5]. The potential for photovoltaic power plants to influence climate change depends on the production share by types of power plants in the specific region.
Bulgaria has taken an active role in the international efforts to help prevent climate change by supporting the concerted actions of the European Union and the wide-ranging package of measures in the energy sector. The widespread use of renewable energy sources (RES) and the implementation of energy efficiency measures are among the priorities of the national energy policy and are complying with the objectives of the new energy policy for Europe. As a result of introduction of Feed-in Tariff (FiT) in 2008 photovoltaic power plants with a total power exceeding 1 GW have been constructed in Bulgaria. In 2014, the FiT dropped out for all ground-based PV power plants and installed on roofs with power over 30 kWp, and FiT currently exists only for small roof and facade photovoltaic systems [6]. This financial motivation, together with the reduction in the prices of equipment for PV power plants, has led in recent years to the construction of a large number of small PV power plants with a capacity of less than 30 kWp on the roofs of buildings and adjacent areas. This causes the current interest and importance of the study of this type of PV power plants in Bulgaria, such as the example in this publication.
A three new roof-mounted 10 kWp grid-connected photovoltaic power plants have been constructed in the Technology Park at the Technical University of Gabrovo, Bulgaria, as part of a project “Competence Center – Intelligent Mechatronic, Eco and Energy Saving Systems and Technologies”. Three different types of technology of the PV modules have been used: mono-crystalline silicon (mono-Si), cadmium telluride (CdTe) and copper indium gallium selenide (CIGS). With the new three power plants, together with the existing photovoltaic power plants in Technical University of Gabrovo with modules of amorphous silicon and poly-crystalline silicon, 5 different photovoltaic materials can be tested simultaneously. A small 500 Wp mono-Si photovoltaic thermal hybrid solar collectors (PVT) PV system is also constructed. The power plants are equipped with a system for monitoring the meteorological and electrical operating parameters, which measures, displays and stores data on solar radiation, temperature, wind speed, currents, voltages, and electrical power of each power plant. 
2. DESIGN AND TECHNICAL DATA FOR THE PHOTOVOLTAIC POWER PLANTS CONSTRUCTED 
The modules of the three roof photovoltaic power plants are mounted on metal constructions – Fig. 1-a). Tilt angle of the photovoltaic modules regarding to the horizon is 33(. As a result of design considerations, the orientation of the photovoltaic modules is deviated by 18.4( degrees to the east – Fig. 1-b). 
[image: image1.png]W0002=1'9/0172.

N=
S

1118

w00ZL=T901

o]

=
5



   [image: image2.png]PWpower plants

PV powerlplants|




	Fig. 1-a). Roof metal construction for the photovoltaic power plants 
	Fig. 1-b). Orientation of the photovoltaic systems


Three different types of technology of the PV modules of the constructed power plants have been used – mono-Si, CdTe and CIGS. Technical data at standard test conditions (STC) of the three different types technology of the PV modules are shown in Table 1 [7,8].

Table 1. Technical data at STC of the three different types technology of the PV modules
	Parameters at STC*
	mono-Si 
	CdTe
	CIGS

	
	by Risen, 
model SYP250M
	by Calyxo, 
model CX4 100/3
	by Hulket, 
model 1100E1

	Nominal power, [Wp]
	250.00
	100.00
	110.00

	Voltage at maximum power, [V]
	30.40 
	72.60
	56.90

	Current at maximum power, [A]
	8.25
	1.38
	1.93

	Open circuit voltage, [V]
	37.50
	72.60
	73.40

	Short circuit current, [A] 
	8.59
	1.53
	2.10

	Maximum system voltage, [Vdc]
	1000
	1000
	1000

	*Notes – STC at: Solar irradiance: 1000 W/m2, Mass of the air: AM = 1.5, Temperature of the PV cell: Tc = 25 (C


Disposition of the three PV power plants on the roof of the Competence Center building at The Technology center of Technical University of Gabrovo is shown in Fig. 2. 
[image: image3.jpg]iy,

R T 2 e
R
BEEOETRE DR

ono-Si





Fig. 2. Disposition of the three PV power plants on the roof of the Competence Center building at the Technology park of Technical University of Gabrovo, Bulgaria
The roof power plant type mono-Si consist of 44 pieces PV modules with maximum power 10 kWp (Fig. 2 and 3). The I-V curves of the mono-Si PV module at different solar irradiation and different cell temperatures are shown in Fig. 4.  

[image: image4.png]


  [image: image5.png]Current(A)

1000W/m*

800W/m*

15 20
Voltage(V)

25




  [image: image6.png]Current(A)

En
6 s
4 25

0
2

-10°C

o —T— T 1
0 10 20 30 40

Voltage(V)




  Fig. 3. Mono-Si PV modules power plant                           Fig. 4-a)                                                Fig. 4-b)
                                                                             Fig. 4. I-V curves of the mono-Si PV module at different irradiation – a)
                                                                               and PV cell temperatures – b)
The roof power plant type CdTe consist of 96 pieces PV modules with maximum power 9.6 kWp (Fig. 2 and 5). Fig. 6 shows relative efficiency at different the cell temperature of the CdTe PV module 100 Wp, model CX4 100/3, Fig. 7 – comparative efficiency at different temperature of the PV cell between CdTe and crystalline (c-Si) silicon material. At temperatures PV cells above 75 (C in the operating zone of Fig. 6 the efficiency of CdTe PV modules is higher than c-Si PV modules.
[image: image7.png]


         [image: image8.png]



  Fig. 5. CdTe PV modules power plant
[image: image9.png]120%

100%

Relative efficiency
(2] 00
o o
N N

N
Q
X

20%

0%

0°C
25°C

50°C
75°C

200 400 600 800 1000
Irradiation, W/m?



      [image: image10.png]Module efficiency, %

—_
N

STC 25°C

25

NMOT @ 45°C

Operating
Temperature

30 35 40 45

50 55 60 65 70 75 80 85 90
Temperature, °C




                 Fig. 6. Performance at different the cell              Fig. 7. Comparative efficiency at different temperature of the
             temperature of the CdTe PV module 100 Wp                  PV cell between CdTe and crystalline silicon material
The roof power plant type CIGS consist of 90 pieces PV modules with maximum power 9.9 kWp (Fig. 2 and 8). I-V curves of the CIGS PV module – model 1100E1, at different solar irradiation and PV cell temperature are shown in Fig. 9. 
[image: image11.png]



 Fig. 8. CIGS PV modules power plant
[image: image12.png]100
== -V 200W/m2
== -V 400W/m2
80 /m
== -V 600W/m2
== -V 800W/m2
60
== -V 1000W/m2
20 —— Pmax_200
~—— Pmax 400
—— Pmax_600
2 —— Pmax 800
—— Pmax_1000




           [image: image13.png]25

Temperature

Characteristics

120

100
== 0ClV
80 __ 25°CI-V
-~ 50°ClV
60 -- 7secry
~—0"CPmax
40 ~25'CPmax
~50"CPmax
T 75"CPmax

20



       
                                   Fig. 9-a)                                                                                        Fig. 9-b)

Fig. 9. I-V curves of the CIGS PV module at different irradiation – a) and PV cell temperatures – b)

A small 500 Wp mono-Si photovoltaic-thermal hybrid solar collectors (PVT) PV system is also constructed – Fig. 2 and connected to a separate grid-connected inverter Fronius Galvo 2.5.
The three PV subsystems on the roof of the building are connected to three sine-wave three-phase grid-tied PV string inverters, model SUN2000-10KTL-M0 (Huawei), that converts the DC power generated by the three PV subsystem with different type PV technologies into AC power and feeds the power into the power grid. The grid-connected PV string inverters synchronized electrical parameters with the power grid. Disposition of the three grid-tied PV string inverters and appearance are shown in Fig. 10. 
[image: image14.png]


  [image: image15.png]


               [image: image16.png]



	Fig. 10. Disposition of the three-phase grid-tied PV string inverters and appearance of the model SUN2000-10KTL-M0 
	Fig. 11. System for monitoring of the PV power plants with model Solar-Log 300


Table 2. Technical data of the sine-wave three-phase grid-tied PV string inverters, model SUN2000-10KTL-M0
	Input
	Output

	Maximum PV power
	14,880 Wp
	Grid connection
	3 phase

	Maximum voltage
	1,100 Vdc
	Rated output power
	10 kW

	Operating voltage range
	(140 ÷ 980) V
	Maximum apparent power
	11 kVA

	Start-up voltage
	200 V
	Rated output voltage
	230/400 Vac

	Full power MPPT voltage range
	(470 ÷ 850) V
	Rated AC grid frequency
	50 Hz

	Rated input voltage
	600 V
	Maximum output current
	16.9 A

	Maximum input current / MPPT
	11 A
	Adjustable power factor (PF)
	0.8 ind ÷ 0.8 cap

	Maximum short-circuit current
	15 A
	Maximum total harmonic distortion (THD)
	≤ 3 %

	Number of MPP trackers
	2
	Maximum efficiency
	98.6 %

	Maximum number of inputs
	2
	
	


The roof PV power plants are equipped with a system for monitoring the meteorological and electrical operating parameters, which measures, displays and stores data on solar radiation, temperature, wind speed, currents, voltages, and electrical power of each power plant. The system for monitoring with smart logger, model Solar-Log 300 [9] – Fig. 11, includes remote alarm function and graphic evaluation on PC. The main technical data of the three sine-wave three-phase grid-tied PV string inverters, model SUN2000-10KTL-M0, are shown in Table 2 [10]. Efficiency curves of the inverters SUN2000-10KTL-M0 at different values of the input voltage are shown in Fig. 12. 
[image: image17.png]Efficiency [%]
100%

98%
96%
94%
92%

90%
0% 20% 40% 60% 80% 100%
Input voltage 470V 600V ——850V

Load [%]





  Fig. 12. Efficiency curves of the inverters SUN2000-10KTL-M0 at different the input voltage
The electrical connection diagram of the individual strings for CdTe and CIGS PV module is shown in Fig. 13. Grounding is done of the installation.
[image: image18.png]1 DOV OBV 126 0mm

0 DOV 0BV 1k

i 2PVIE QHIRY 1ad O

i 2PVIE QHIRY 128 G

o cmpT

Fut

RIS

i

10 DOV OBV 126 0mm

o copanet

FU2

o coponeT

Fu3

0 DOV 0BV Tk

i 2PVIE QHIRY 1ad O

o copnaL

i 2PVIE QHIRY 118 G

o T

o T

o T3

o N3

CdTe/CIGS





Fig. 13. Schemes with basic wiring diagram of the individual strings for CdTe and CIGS PV module
Communications with the inverters SUN2000-10KTL-M0 and smart logger Smart-Log 300 can be with access over a public network (Fig. 14) and by access over a local ethernet and WiFi (Fig. 15).
[image: image19.png]~—— RS485 communications
cable SmartLogger
— Power cable WebUI
— Ethernet cable Smart loger
SUN2000 lj'“\ Solar—Log 300 ,_.D

APP K
FusionHome APP

[
Py modue L e Y
Inverter 1

).
L -] Mgmt system WebUI
EE 4G Antenna

: A

Combiner box ~ Smart power g yor grig
sensor

1S06N00036



 [image: image20.png]SmartLogger

WebUI
~—— RS485 communications
cable
— Power cable Sun2000
APP

— Ethernet cable

PV module
Inverter 1

g

D’\ SmartLogger
\ 1000A

Router
: BEEBBJC\

]

. _FusionHome APP

JE3Y

Mgmt system WebUI
(=]
=la
Combiner box Smart power

sensor

Power grid
1S06N00037




	Fig. 14. Communications with the inverters and smart logger by access over a public network
	Fig. 15. Communications with inverters by access over a local ethernet and WiFi


3. INITIAL DATA FROM SOFTWARE FOR MONITORING OF METEOROLOGICAL AND ELECTRICAL PARAMETERS
The system for monitoring of the roof PV power plants is done in two ways: direct communication with the three-phase sine-wave inverters via RS485, WLAN, WiFi/4G or via mobile FusionSolar App and detail monitoring from smart logger Solar-Log 300. Fig. 16 shows direct communications with inverters SUN2000-10KTL-M0 over WiFi with FusionHome App. The mobile app displays grid connected, daily, monthly and yearly energy yield. The roof PV power plants was put into operation in May 2020. 
[image: image21.png]15:20 9 4 0 62%
< Device status

SUN2000-10KTL-MO
Grid connected

cssescnne peceeccanss]]
: v
H T
. .
o) 67590 : A
o | A2820v5208 PPN A
EEHREA

6.898KW

v w7y
.

i

.

Do a7

~
O

Device
status



      [image: image22.png]15184, @

< Energy yield statistics

102020
Energy yield(Wh)
000
6000
s000
000
000
2000 I I ”
1000
o 111 |
0 s s 2 s owo w2 oz oW
Day
Time Energy yield(kWh)
2840112020 64.36
29-1041-2020 6212
3040112020 63.35
Energy yield

statistics



      [image: image23.png]< Energy yield statistics

Day Month History

0

Ency )

o 1 I I I I h

Eneroyyield
statistics.




Fig. 16. Communications with inverters SUN2000-10KTL-M0 over WiFi with FusionHome App
Detail data for the meteorological and electrical operating parameters of the roof PV power plants are received from smart logger Solar-Log 300. The system for monitoring by the smart logger measures, displays in real time and stores data on solar radiation, temperature, wind speed, currents, voltages, electrical power, energy yield and registered events of each power plant. Fig. 17 and 18 shows monitoring in real time of the yield data and energy flow from PV power plants to power grid.
[image: image24.png](@solor-Log™

Engiish

Yield data

7 VELDDATA | DIAGNOSTICS | g CONFIGURATION | 3.

Welcome to the Main Menu
of the Solar-Log 300

Current values / Cockpit

@ Solar-Log




           [image: image25.png](@solor-Log™  Engish ¥ VELDDATA | DIAGNOSTICS

Welcome to the Main Menu
of the Solar-Log 300

Yield data / Current values / Energy flow

26.42 kW “ y 9
SR
L

1

i sececccced

26.42 kW

Feedin

© CONAIGURATION | 3

@ Solar-Log




	Fig. 17. Monitoring of the yield data
	Fig. 18. Monitoring of the energy flow


The system for monitoring displays details individually for each inverter as status (on-grid or off-grid), the daily change of the input DC voltage, currents, powers and AC output AC and temperature – Fig. 19 and 20. The values can be displayed for a selected period of time. The software to the system for monitoring visualizes daily, monthly and annual electricity production of the PV power plants. All values of the electrical parameters, temperature, solar irradiation, status of the inverters, errors and events are stored and can be exported to CSV file – Fig. 21. When the actual yield differs from the target yield, the monitoring system sends a notification (email message et.al).
[image: image26.png]Craphicis cached

Q [0 8 ©

B
250620120252 0M) @

nw

0w

=
=
o

@

=

a0,



 [image: image27.png]Graphic s cached

weun |8 O

=wvaaes

2506201203230 Mm) @

=
-
©

s
ot ap woes

o Jsos

aom





	Fig. 19. The inverter details of the power plant with mono-Si PV modules
	Fig. 20. The inverter details of the power plant with CIGS PV modules


[image: image28.png]utoSave export_minxl: Plamen
File  Home Insert Pagelayout Formulas Data Review View Help  Acrobat 1% Share 7 Comments
L caibn v e General - B O BP 8rsE iy O %
[ACopy v LI Fill ~
2 Sromammer | 1Y E Bl vergeascener ~ | 08~ 9% 9 B | GO TR L. TR Qe A suar |
Clipboard ~ Font ~ Alignment ~ Number ~ Styles Cells Editing Ideas Sensitivity ~
c2 - 5 1 v
A B < D E F G H I J K L M N o P Q R S T u v W X Y[+
1 #Date Time INV Pac [W] DaySum [VStatus Error Pdcl[W] Pdc2 [W] Udcl[V] Udc2[V] Temp [°C] Idcl[mA] Idc2 [mA] Uacl[V] Uac2[V] Uac3[V] INV Pac [W]  DaySum [V Status Error Pdcl [W] Pdc2 [W] Udcl
2 | 5.6.2020 17:25:00| 11 2552 50820 5 0 1265 1364 546 543 39 2316 2511 244 247 244 2 1436 27740 5 0 1494 5
3 | 5.6.2020 17:20:00| 1 2547 50610 5 0 1262 1363 545 540 39 2311 2518 244 247 244 2 1434 27620 5 0 1491 6
4 | 5.6.2020 17:15:00) 1 3137 50400 5 0 1559 1664 550 547 39 2833 3036 243 246 244 2 1755 27510 5 0 1815 5
5 | 5.6.2020 17:10:00| 1 1874 50150 5 0 925 1015 538 532 39 1720 1907 243 246 244 2 1071 27370 5 0 1122 5
6 | 5.6.2020 17:05:00| 1 1815 49990 5 0 895 984 536 529 40 1668 1860 243 246 244 2 1033 27270 5 0 1082 5
7 | 5.6.2020 17:00:00| 1 3029 49870 5 0 1505 1609 545 540 40 2757 2977 243 246 244 2 1671 27210 5 0 1734 5
8 | 5.6.2020 16:55:00) 1 3991 49580 5 0 1990 2106 549 546 40 3622 3851 243 246 243 2 2192 27040 5 0 2262 5
9 | 5.6.2020 16:50:00| 1 2429 49250 5 0 1205 1302 546 539 40 2203 2416 242 245 243 2 1378 26860 5 0 1434 5
10| 5.6.2020 16:45:00) 1 2304 49050 5 0 1141 1239 539 535 40 2117 2311 242 245 243 2 1302 26750 5 0 1356 5
11| 5.6.2020 16:40:00) 1 2343 48860 5 0 1161 1259 538 535 41 2157 2351 242 245 242 2 1313 26640 5 0 1368 5
12| 5.6.2020 16:35:00) 1 3412 48660 5 0 1698 1809 545 543 41 3110 3331 242 245 242 2 1883 26530 5 0 1949 5
13| 5.6.2020 16:30:00) 1 3137 48380 5 0 1558 1666 541 540 42 2878 3081 241 245 242 2 1753 26380 5 0 1815 5
14| 5.6.2020 16:25:00 1 2960 48120 5 0 1468 1577 535 532 42 2742 2960 241 245 242 2 1636 26230 5 0 1699 5
15| 5.6.2020 16:20:00) 1 4492 47890 5 0 2241 2369 538 542 43 4161 4368 242 245 242 2 2432 26110 5 0 2512 5
16| 5.6.2020 16:15:00) 1 5304 47520 5 0 2644 2789 541 540 43 4887 5158 242 245 243 2 2850 25900 5 0 2942 5
17| 5.6.2020 16:10:00) 1 5500 47240 5 0 2741 2892 548 544 42 5001 5315 241 245 242 2 3001 25750 5 0 3090 5
18| 5.6.2020 16:05:00) 1 3479 46580 5 0 1728 1846 541 539 43 3190 3416 241 244 242 2 1923 25400 5 0 1987 6
19| 5.6.2020 16:00:00) 1 5152 46330 5 0 2569 2712 542 544 43 4739 4982 242 245 242 2 2798 25260 5 0 2885 5
20| 5.6.2020 15:55:00| 1 5177 45850 5 0 2583 2724 542 536 44 4762 5072 241 245 242 2 2825 25000 5 0 2912 5
21 5.6.2020 15:50:00| 1 5184 45470 5 0 2585 2727 535 534 44 4823 5101 241 245 242 2 2812 24790 5 0 2901 6
22| 5.6.2020 15:45:00| 1 6131 44990 5 0 3056 3213 540 539 44 5658 5955 242 245 242 2 3276 24540 5 0 3380 6
23| 5.6.2020 15:40:00| 1 6987 44470 5 0 3482 3654 540 544 43 6444 6717 242 245 242 2 3733 24260 5 0 3848 5
24| 5.6.2020 15:35:00| 1 5549 43890 5 0 2767 2915 539 543 43 5130 5360 241 245 242 2 2988 23940 5 0 3083 6
25| 5.6.2020 15:30:00| 1 5753 43410 5 0 2862 3022 536 542 43 5338 5571 241 245 242 2 3094 23680 5 0 3194 6
26| 5.6.2020 15:25:00| 1 7477 42930 5 0 3723 3911 543 545 43 6856 7n 242 245 242 2 3956 23430 5 0 4082 6
27| 5.6.2020 15:20:00| 1 6951 42320 5 0 3462 3634 548 548 42 6312 6630 242 246 243 2 3711 23110 5 0 3824 6
28| 5.6.2020 15:15:00| 1 5937 41750 5 0 2956 3114 545 552 42 5418 5637 242 246 243 2 3218 22800 5 0 3317 6
29| 5.6.2020 15:10:00| 1 4889 41240 5 0 2433 2578 547 548 41 4444 4697 242 245 242 2 2680 22530 5 0 2762 6 v
export min | Sheetl | @) b »
El 1 L + 100%





Fig. 21. CSV export data of the system for monitoring 
4. ASSESSMENT OF THE ECOLOGICAL EQUIVALENT OF THE SAVED ENERGY IN BULGARIA
In Bulgaria, a mandatory state “Ordinance № E-RD-04-3 from 4.05.2016 on eligible measures for the implementation of energy savings in final consumption, ways of demonstrating the energy savings achieved, the requirements for their assessment methodologies and ways of confirmation“ [11] applies. This state ordinance includes an Appendix 3 with Reference values of the conversion factor considering the losses for extraction / production and transmission of energy, including fuels, as well as an Appendix 4 with Reference values of the coefficient of ecological equivalent of energy for different fuels – Table 3. A Specialized Commission on Electricity at the National Agency for Sustainable Energy Development, with the participation of the author of this publication, has developed a Methodology for estimating energy savings when installing photovoltaic systems [12], according to the Ordinance.
Table 3. Reference values of the conversion factor considering the losses for extraction / production and transmission of energy, including fuels, and Reference values of the coefficient of ecological equivalent of energy
	Type of energy resource / energy
	Conversion factor from FES to PES, considering energy losses
	Ecological equivalent coefficient

	
	ep
	fi

	
	[-]
	[gCO2/kWh]

	Industrial gas oil, diesel
	1.10
	267

	Fuel oil
	1.10
	279

	Natural gas
	1.10
	202

	Propane-butane
	1.10
	227

	Black coal
	1.20
	341

	Lignite / brown coal
	1.20
	364

	Anthracite coal
	1.20
	354

	Coal briquettes
	1.25
	351

	Firewood, pellets
	1.05
	43

	Heat from district heating
	1.30
	290

	Electrical energy
	3.00
	819


The analysis of the initial data from the monitoring systems of the new photovoltaic power plants in the Technology Park of the Technical University - Gabrovo, allows calculation of the necessary parameters for assessment of their impact on reducing carbon emissions and climate change. Fig. 22 shows the web-view of the software for monitoring the 30 kWp (mono-Si, CdTe and CIGS) grid-connected power plants on the roof of the Gabrovo Tech Park showing CO2 emissions avoided for the period from the launch of the power plant in May 2020 to July 2021, which are a total of 32.14 tons.

[image: image29.png][EEET W solar-Log

ENGLISH ~  FAQ

~ Plamen Tsankov
~ Gabrovo Tech Park -

Technical University of
Gabrovo

~ Graphic

> Events

> Welcome
> Plants

> Map

© 2021 Solar-Log GmbH

%9 7 Overview of all Years

dTe

INV 2 monoSi ‘ INV 3 CIGS ‘

30 MWh

25 MWh

20 MWh

15 MWh

10 MWh

5 MWh

Lifetime Total

Feed-in Power Pac ow Yield . 4591 MWhQ
Generator Power Pdc —w

Inverter Efficiency n 0 % Specific Yield 1610.79 kWh/kWp
Status, Idle Initializing, 2x Idle No ... ® Actual Value

Error. ®

CO= emissions avoided in total

A PLAMEN TSANKOV

cy.Policy | GTC | Right of revocation for end customers | Price List | Imprint | Licenses




Fig. 22. Software for monitoring the 30 kWp grid-connected power plan on the roof of the Gabrovo Tech Park showing CO2 emissions avoided for the period from the launch of the power plant in May 2020 to July 2021
The Android (Fig. 23 - left) and Web-based (Fig. 23 - right) software for monitoring the small hybrid PVT system (Fig. 2) are configured also to directly calculate the environmental benefits of its operation. Fig. 23 shows an exemplary screenshots indicating the saved kilograms of CO2 emissions from the beginning of the system operation, as well as the corresponding number of saved trees or gained kilometers of movement of an airplane or a car with an internal combustion engine. The saved CO2 emissions for the period from the launch of the power plant in May 2020 to July 2021 are about 950 kilograms.
[image: image30.jpg]B all @D 88,

TU Gabrovo Tech park &
Earnings
Today 0.00
August BGN 24.96
2021 BGN 232.54
Total BGN 428.34

CO, Savings total

Fitf) 945.91

Kilogram

E—-% 24
= Kilometres
& =

= Trees

e 3,796
— Kilometres
m Jdh 5 &

Current History Earnings Profile



   [image: image31.png]B (838 nenpouereny) - plame: X

[ Nuuna cipanua cnepcona X | B Google Mpesonau X | @ Arenunasaycroiunso ene; X | @ Hos pasnen X @ TU Gabrovo Tech park X+ o = X
< C @ solarweb.com/PvSystems/PvSystem?pvSystemld=c54add2c-125e-4b7d-a864-87f6ef52e523 & Q % QOO * L0 &N @ H
Mpunoxervs  Jr Bookmarks Wl plamentsankov - Ya.. @ Kanewaap - 2ou. A-.. (fl§ BxoaYMVC P Webmail - Lighting... @ Lighting_2021-0n.. @ Municipality Gabro.. @) The Nature of Light.. » | [ Opymormerkn | [E] Crucok 3a uetere

Fronius TU Gabrovo Tech park

OVERVIEW | ANALYSIS | ENERGY BALANCE | REPORTS | SERVICE MESSAGES | SETTINGS PREMIUM

CURRENT POWER ENERGY BALANCE TODAY EARNING

773 kWh
August 2021

28.57 BoN

COz SAVINGS TOTAL

ow Y 95394
Utilization 0 % 00h 12h 18h 00h .
TU GABROVO TECH PARK GABROVO (i)

E BN

o
0

= 21 21°¢ U
My PV systems > TU Gabrovo Tech park a Gototop

20:42
16.82021 .




Fig. 23. Software for monitoring the PVT system showing environmental benefits of its operation
4. CONCLUSIONS


With the construction of the new three mono-Si, CdTe and CIGS power plants presented, together with the existing photovoltaic power plants with modules of a-Si and p-Si, 5 different photovoltaic materials can be tested simultaneously in the new laboratory at the Technology park of the Technical University of Gabrovo. The initial measured and stored comparative data from software for monitoring of meteorological and electrical operating parameters of the three different PV module materials of solar radiation, temperature, wind speed, currents, voltages, and electrical power of each power plant, confirm the operability and functionality for future research of the new photovoltaic power plants constructed. Their modern systems for monitoring the meteorological and electrical operating parameters allow for a detailed analysis of the produced electricity and assessment of the impact on climate change of a similar type of widespread in Bulgaria roof-mounted PV power plants.
The carbon savings achieved by the small rooftop photovoltaic power plants in the present study are relatively small for major impacts on climate change but are useful with the ability to assess the savings potential of different photovoltaic module technologies. The considered technical solutions for roof PV power plants with power up to 30 kWp and their results are significant for the current stage of development of photovoltaic electricity in Bulgaria, as only for such power plants there is still FiT. A study in the register of newly built photovoltaic power plants in Bulgaria [13] shows that in 2020, 759 new ones were built, of which 727, or 96% have a capacity of up to 30 kWp.

The technical solutions developed in this study and the results obtained can be useful for the correct choice of technology photovoltaic modules and other elements of photovoltaic power plants, as well as for assessing their impact on climate change in Bulgaria and other regions with similar weather conditions and profiles. of energy sources in their electricity systems.
5. ACKNOWLEDGEMENT

This work was supported by the European Regional Development Fund within the OP “Science and Education for Smart Growth 2014 - 2020”, Project CoC “Smart Mechatronic, Eco- And Energy Saving Systems And Technologies“, № BG05M2OP001-1.002-0023.
6. REFERENCES


[1] Pavlovic T., Tsankov P.T., Cekić N.D., Radonjić Mitić I.S. (2020) Photovoltaic Solar Energy Conversion. In: Pavlovic T. (eds) The Sun and Photovoltaic Technologies. Green Energy and Technology. Springer, Cham.
[2] Wurster, S., & Hagemann, C. (2019). Expansion of Renewable Energy in Federal Settings: Austria, Belgium, and Germany in Comparison. The Journal of Environment & Development, 107049651988748.
[3] Gugler, K., Haxhimusa, A., & Liebensteiner, M. (2021). Effectiveness of climate policies: Carbon pricing vs. subsidizing renewables. Journal of Environmental Economics and Management, 106.
[4] Yang, Z., Liu, P., Cheng, L., Liu, D., Ming, B., Li, H., Xia, Q. Sizing utility-scale photovoltaic power generation for integration into a hydropower plant considering the effects of climate change: A case study in the Longyangxia of China, (2021) Energy, 236, art. no. 121519.
[5] Santoyo-Castelazo, E., Solano-Olivares, K., Martínez, E., García, E. O., & Santoyo, E. (2021). Life cycle assessment for a grid-connected multi-crystalline silicon photovoltaic system of 3 kWp: A case study for Mexico. Journal of Cleaner Production, 316.
[6] Tsankov, P., M. Yovchev, Technical and Economic Development of the Photovoltaic Electricity in Bulgaria, Contemporary Materials, X-2 (2019), pp. 119-131.
[7] Calyco – Data sheet for CdTe PV modules CX4 100/3.
[8] Hulket – Data sheet for CIGS PV modules 1100E1.
[9] https://www.solar-log.com/manuals/manuals/en_GB/SolarLog_Manual_3x_EN.

[10] Inverters SUN2000-(3KTL-10KTL)-M0 – User Manual, Huawei Technologies, 2019.
[11] ORDINANCE № E-RD-04-3 of 4.05.2016 on eligible measures for the implementation of energy savings in final consumption, ways of demonstrating the energy savings achieved, the requirements for their assessment methodologies and ways of confirmation, Official Journal of Republic of Bulgaria, no. 38 of 20.05.2016, in force since 20.05.2016, amended. and add., no. 79 of 25.09.2018.

[12] https://portal.seea.government.bg/bg/Methodics/Methodics/Methodics
[13] https://portal.seea.government.bg/bg/ByProducerAndEnergyObject
